## Introduction and Notes
Points Schedule Introduction:
1 | The Points Schedule is a required design and as-built document per UFC 3-410-02. Typically the first draft is provided in the 65% design submittal.
2 | These Points Schedules are templates to be used as a starting point for designers. These templates meet the requirements outlined in UFC 3-410-02 'DDC for HVAC and other Building Control Systems'.
3 | The templates are not intended to be the final Points Schedule for a project. The formatting can be the same but every project is different, with differing designs and project requirements that will require different point attributes.
4 | The Points Schedule process is started by the designer and provided as a part of the design. Coordination with the installation or building owner is required to develop a Points Schedule that will meet their needs.
5 | The controls contractor/installer will complete the Points Schedule and will provide it as a part of the as-built drawings.
6 | The Index tab provides the tab number with it's cooresponding system type.
See UFC 3-410-02 Appendix D for detailed information on the Points Schedules
In general:
The controls contractor is responsible for submitting a completed Points Schedule.
The Points Schedule uses brackets and symbology to provide clarity
|  | Symbol |  | Meaning
|  | [___] |  | “Square brackets” (“[___]”) are used to indicate selections or entries made by the designer
|  | <___> |  | “Angle brackets” (“<___>”) are used to indicate selections or entries that must be made by the building control system contractor.
|  | ~ |  | A tilde (“~”) is used in a cell where there could be a valid entry, but no entry is required (i.e. it’s specifically used to mean “I could have put a value here but I chose not to enter one”)
|  |  | or N/A | An “N/A” (or a greyed out cell, or a combination of N/A and a greyed out cell) is used when there is no possibility of a valid entry for that particular cell.

## Index
Worksheet TAB | Description
Notes | Notes
Index | Index
1 | CONVENTIONAL MZ WITH RETURN FAN
2 | CONVENTIONAL MZ WITHOUT RETURN FAN
3 | BYPASS MZ WITH RETURN FAN
4 | BYPASS MZ WITHOUT RETURN FAN
5 | NEUTRAL DECK MZ WITH RETURN FAN
6 | NEUTRAL DECK MZ WITHOUT RETURN FAN

## 1
CONVENTIONAL MULTIZONE WITH RETURN FAN
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RF-S | RETURN FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-LL-SP | MIXED AIR TEMPERATURE LOW LIMIT SETPOINT | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-LL | ZONE TEMPERATURE LOW LIMIT SETPOINT |  | [60 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-T-HL | ZONE TEMPERATURE LOW LIMIT SETPOINT |  | [80 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [ V ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ V ] | [ ~ ] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
SUPPLY FAN CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [50%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-SP | ZONE DAMPER COMMAND SETPOINT |  | [95%] |  |  |  | C | VO | V | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-C-EFF | MAXIMUM (EFFECTIVE) ZONE DAMPER COMMAND |  |  | 0-100% OPEN |  |  |  | V | V | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SUPPLY FAN CONTROL PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
RETURN FAN CONTROL | RF-C | RETURN FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RF-C-MIN | RETURN FAN COMMAND MINIMUM |  | [40%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| OFFSET | FAN COMMAND OFFSET |  | [10 %] | 0-100% |  | [~] | C | VO | [~] |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
OUTSIDE AIRFLOW | MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] or [RESET PER DCV] |  |  |  | C | ~ | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| OA-F | OUTSIDE AIR FLOW | <___> |  | <0-___ CFM> | AI |  |  | V | [ V ] | X | OA-F IS LESS THAN MINOA-F-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OUTSIDE AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
MIXED AIR TEMPERATURE CONTROL [WITH ECONOMIZER] | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T | MIXED AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT |  | [___] | <___> |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-S | ECONOMIZER STATUS | [6 empty] | V | [ V ] | X | [9 empty] | <___> | <___> | <___> | <___>
| MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO |  |  | VO | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MIXED AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
HOT DECK CONTROL | HD-T | HOT DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HD-T-SP | HOT DECK TEMPERATURE SETPOINT | <___> | [ RESET ] | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTG-OO-LL-SP | HEATING ON/OFF LOW LIMIT SETPOINT | <___> | [25%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTG-OO-HL-SP | HEATING ON/OFF HIGH LIMIT SETPOINT | <___> | [65%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| HD-V-C | HOT DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HEATING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
COLD DECK CONTROL | CD-T | COLD DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CD-T-SP | COLD DECK TEMPERATURE SETPOINT |  |  | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| CLG-OO-LL-SP | COOLING ON/OFF LOW LIMIT SETPOINT | <___> | [5%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| CLG-OO-HL-SP | COOLING ON/OFF HIGH LIMIT SETPOINT | <___> | [15%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| CD-V-C | COLD DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COOLING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE [1] TEMPERATURE CONTROL | ZN1-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN1-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-DAT | ZONE DISCHARGE AIR TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| [ZN1-OCC] | ZONE OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE [2] TEMPERATURE CONTROL | ZN2-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN2-DAT | ZONE DISCHARGE AIR TEMPERATURE |  |  | <___> | AI | [~] |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| [ZN1-OCC] | ZONE OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OTHER POINTS | RA-T | RETURN AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [ ~ ] | [ ~ ] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
[DCV: CO2 POINTS] | ZN-CO2-EFF | MAXIMUM ZONE CO2 | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-CO2 | ZONE 1 CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN1-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-CO2 | ZONE 2 CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN2-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OA-F-SP | OUTSIDE AIR FLOW SETPOINT | <___> | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MAX | MAXIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[DCV: OCC SENSOR POINTS] | OA-F-SP | OUTSIDE AIR FLOW SETPOINT | <___> | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-OCC | ZONE 1 OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-OCC | ZONE 2 OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MINOA-F-MAX | MAXIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 2
CONVENTIONAL MULTIZONE WITHOUT RETURN FAN
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-LL-SP | MIXED AIR TEMPERATURE LOW LIMIT SETPOINT | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-LL | ZONE TEMPERATURE LOW LIMIT SETPOINT |  | [60 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-T-HL | ZONE TEMPERATURE LOW LIMIT SETPOINT |  | [80 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [ V ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ V ] | [ ~ ] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
SUPPLY FAN CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [50%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-SP | ZONE DAMPER COMMAND SETPOINT |  | [95%] |  |  |  | C | VO | V | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-C-EFF | MAXIMUM (EFFECTIVE) ZONE DAMPER COMMAND |  |  | 0-100% OPEN |  |  |  | V | V | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SUPPLY FAN CONTROL PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
OUTSIDE AIRFLOW | MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] or [RESET PER DCV] |  |  |  | C | ~ | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| OA-F | OUTSIDE AIR FLOW | <___> |  | <0-___ CFM> | AI |  |  | V | [ V ] | X | OA-F IS LESS THAN MINOA-F-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OUTSIDE AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
MIXED AIR TEMPERATURE CONTROL [WITH ECONOMIZER] | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T | MIXED AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT |  | [___] | <___> |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-S | ECONOMIZER STATUS | [6 empty] | V | [ V ] | X | [9 empty] | <___> | <___> | <___> | <___>
| MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO |  |  | VO | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MIXED AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
HOT DECK CONTROL | HD-T | HOT DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HD-T-SP | HOT DECK TEMPERATURE SETPOINT | <___> | [ RESET ] | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTG-OO-LL-SP | HEATING ON/OFF LOW LIMIT SETPOINT | <___> | [25%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTG-OO-HL-SP | HEATING ON/OFF HIGH LIMIT SETPOINT | <___> | [65%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| HD-V-C | HOT DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HEATING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
COLD DECK CONTROL | CD-T | COLD DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CD-T-SP | COLD DECK TEMPERATURE SETPOINT |  |  | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| CLG-OO-LL-SP | COOLING ON/OFF LOW LIMIT SETPOINT | <___> | [5%] | 0-100% |  |  | C | V | [ V ] | [10 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| CLG-OO-HL-SP | COOLING ON/OFF HIGH LIMIT SETPOINT | <___> | [15%] | 0-100% |  |  | C | V | [ V ] | [10 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| CD-V-C | COLD DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COOLING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE [1] TEMPERATURE CONTROL | ZN1-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN1-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-DAT | ZONE DISCHARGE AIR TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| [ZN1-OCC] | ZONE OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE [2] TEMPERATURE CONTROL | ZN2-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN2-DAT | ZONE DISCHARGE AIR TEMPERATURE |  |  | <___> | AI | [~] |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| [ZN1-OCC] | ZONE OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OTHER POINTS | RA-T | RETURN AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [ ~ ] | [ ~ ] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
[DCV: CO2 POINTS] | ZN-CO2-EFF | MAXIMUM ZONE CO2 | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-CO2 | ZONE 1 CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN1-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-CO2 | ZONE 2 CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN2-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OA-F-SP | OUTSIDE AIR FLOW SETPOINT | <___> | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MAX | MAXIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[DCV: OCC SENSOR POINTS] | OA-F-SP | OUTSIDE AIR FLOW SETPOINT | <___> | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-OCC | ZONE 1 OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-OCC | ZONE 2 OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MINOA-F-MAX | MAXIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 3
HOT DECK BYPASS MULTIZONE WITH RETURN FAN
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RF-S | RETURN FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-LL-SP | MIXED AIR TEMPERATURE LOW LIMIT SETPOINT | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-LL | ZONE TEMPERATURE LOW LIMIT SETPOINT |  | [60 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-T-HL | ZONE TEMPERATURE LOW LIMIT SETPOINT |  | [80 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [ V ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ V ] | [ ~ ] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
SUPPLY FAN CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [50%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-DVC-SP | ZONE DAMPER/VALVE COMMAND SETPOINT |  | [95%] |  |  |  | C | VO | V | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-DVC-C-EFF | MAXIMUM (EFFECTIVE) ZONE DAMPER/VALVE COMMAND |  |  | 0-100% OPEN |  |  |  | V | V | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SUPPLY FAN CONTROL PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
RETURN FAN CONTROL | RF-C | RETURN FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RF-C-MIN | RETURN FAN COMMAND MINIMUM |  | [40%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| OFFSET | FAN COMMAND OFFSET |  | [10 %] | 0-100% |  | [~] | C | VO | [~] |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
OUTSIDE AIRFLOW | MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] or [RESET PER DCV] |  |  |  | C | ~ | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| OA-F | OUTSIDE AIR FLOW | <___> |  | <0-___ CFM> | AI |  |  | V | [ V ] | X | OA-F IS LESS THAN MINOA-F-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OUTSIDE AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
MIXED AIR TEMPERATURE CONTROL [WITH ECONOMIZER] | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T | MIXED AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT |  | [___] | <___> |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-S | ECONOMIZER STATUS | [6 empty] | V | [ V ] | X | [9 empty] | <___> | <___> | <___> | <___>
| MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO |  |  | VO | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MIXED AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
COLD DECK CONTROL | CD-T | COLD DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CD-T-SP | COLD DECK TEMPERATURE SETPOINT |  |  | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| CLG-OO-LL-SP | COOLING ON/OFF LOW LIMIT SETPOINT | <___> | [5%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| CLG-OO-HL-SP | COOLING ON/OFF HIGH LIMIT SETPOINT | <___> | [15%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| CD-V-C | COLD DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COOLING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE [1] TEMPERATURE CONTROL | ZN1-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN1-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-DAT | ZONE DISCHARGE AIR TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| ZN1-V-C | ZONE VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~]
| ZONE COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| [ZN1-OCC] | ZONE OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE [2] TEMPERATURE CONTROL | ZN2-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN2-DAT | ZONE DISCHARGE AIR TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN2-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| ZN2-V-C | ZONE VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~]
| ZONE COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| [ZN2-OCC] | ZONE OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OTHER POINTS | RA-T | RETURN AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [ ~ ] | [ ~ ] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
[DCV: CO2 POINTS] | ZN-CO2-EFF | MAXIMUM ZONE CO2 | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-CO2 | ZONE 1 CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN1-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-CO2 | ZONE 2 CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN2-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OA-F-SP | OUTSIDE AIR FLOW SETPOINT | <___> | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MAX | MAXIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[DCV: OCC SENSOR POINTS] | OA-F-SP | OUTSIDE AIR FLOW SETPOINT | <___> | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-OCC | ZONE 1 OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-OCC | ZONE 2 OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MINOA-F-MAX | MAXIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[SPACE HUMIDITY CONTROL] | ZN-RH-SP | ZONE RELATIVE HUMIDITY SETPOINT | <___> | [70%] | 0-100% |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-RH-SP-DB | ZONE RELATIVE HUMIDITY SETPOINT DEADBAND | <___> | [5%] | 0-100% |  |  | C | [12 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-RH | ZONE 1 RELATIVE HUMIDITY | <___> | <___> | 0-100% | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-RH | ZONE 2 RELATIVE HUMIDITY | <___> | <___> | 0-100% | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 4
HOT DECK BYPASS MULTIZONE WITHOUT RETURN FAN
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-LL-SP | MIXED AIR TEMPERATURE LOW LIMIT SETPOINT | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-LL | ZONE TEMPERATURE LOW LIMIT SETPOINT |  | [60 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-T-HL | ZONE TEMPERATURE LOW LIMIT SETPOINT |  | [80 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [ V ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ V ] | [ ~ ] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
SUPPLY FAN CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [50%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-DVC-SP | ZONE DAMPER/VALVE COMMAND SETPOINT |  | [95%] |  |  |  | C | VO | V | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-DVC-C-EFF | MAXIMUM (EFFECTIVE) ZONE DAMPER/VALVE COMMAND |  |  | 0-100% OPEN |  |  |  | V | V | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SUPPLY FAN CONTROL PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
OUTSIDE AIRFLOW | MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] or [RESET PER DCV] |  |  |  | C | ~ | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| OA-F | OUTSIDE AIR FLOW | <___> |  | <0-___ CFM> | AI |  |  | V | [ V ] | X | OA-F IS LESS THAN MINOA-F-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OUTSIDE AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
MIXED AIR TEMPERATURE CONTROL [WITH ECONOMIZER] | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T | MIXED AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT |  | [___] | <___> |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-S | ECONOMIZER STATUS | [6 empty] | V | [ V ] | X | [9 empty] | <___> | <___> | <___> | <___>
| MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO |  |  | VO | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MIXED AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
HOT DECK CONTROL | HD-T | HOT DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HD-T-SP | HOT DECK TEMPERATURE SETPOINT | <___> | [ RESET ] | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HD-V-ENA | HOT DECK VALVE ENABLE | <___> | [65%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| HD-V-DIS | HOT DECK VALVE DISABLE | <___> | [15%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| HD-V-C | HOT DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HEATING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
COLD DECK CONTROL | CD-T | COLD DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CD-T-SP | COLD DECK TEMPERATURE SETPOINT |  |  | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| CLG-OO-LL-SP | COOLING ON/OFF LOW LIMIT SETPOINT | <___> | [5%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| CLG-OO-HL-SP | COOLING ON/OFF HIGH LIMIT SETPOINT | <___> | [15%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| CD-V-C | COLD DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COOLING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE [1] TEMPERATURE CONTROL | ZN1-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN1-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-DAT | ZONE DISCHARGE AIR TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| ZN1-V-C | ZONE VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~]
| ZONE COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| [ZN1-OCC] | ZONE OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE [2] TEMPERATURE CONTROL | ZN2-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN2-DAT | ZONE DISCHARGE AIR TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN2-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| ZN2-V-C | ZONE VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~]
| ZONE COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| [ZN2-OCC] | ZONE OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OTHER POINTS | RA-T | RETURN AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [ ~ ] | [ ~ ] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
[DCV: CO2 POINTS] | ZN-CO2-EFF | MAXIMUM ZONE CO2 | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-CO2 | ZONE 1 CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN1-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-CO2 | ZONE 2 CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN2-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OA-F-SP | OUTSIDE AIR FLOW SETPOINT | <___> | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MAX | MAXIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[DCV: OCC SENSOR POINTS] | OA-F-SP | OUTSIDE AIR FLOW SETPOINT | <___> | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-OCC | ZONE 1 OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-OCC | ZONE 2 OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MINOA-F-MAX | MAXIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[SPACE HUMIDITY CONTROL] | ZN-RH-SP | ZONE RELATIVE HUMIDITY SETPOINT | <___> | [70%] | 0-100% |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-RH-SP-DB | ZONE RELATIVE HUMIDITY SETPOINT DEADBAND | <___> | [5%] | 0-100% |  |  | C | [12 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-RH | ZONE 1 RELATIVE HUMIDITY | <___> | <___> | 0-100% | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-RH | ZONE 2 RELATIVE HUMIDITY | <___> | <___> | 0-100% | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 5
NEUTRAL DECK MULTIZONE WITH RETURN FAN
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RF-S | RETURN FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-LL-SP | MIXED AIR TEMPERATURE LOW LIMIT SETPOINT | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-LL | ZONE TEMPERATURE LOW LIMIT SETPOINT |  | [60 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-T-HL | ZONE TEMPERATURE LOW LIMIT SETPOINT |  | [80 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [ V ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ V ] | [ ~ ] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
SUPPLY FAN CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [50%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-SP | ZONE DAMPER COMMAND SETPOINT |  | [95%] |  |  |  | C | VO | V | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-C-EFF | MAXIMUM (EFFECTIVE) ZONE DAMPER COMMAND |  |  | 0-100% OPEN |  |  |  | V | V | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SUPPLY FAN CONTROL PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
RETURN FAN CONTROL | RF-C | RETURN FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RF-C-MIN | RETURN FAN COMMAND MINIMUM |  | [40%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| OFFSET | FAN COMMAND OFFSET |  | [10 %] | 0-100% |  | [~] | C | VO | [~] |  |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  |  | <___>
OUTSIDE AIRFLOW | MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] or [RESET PER DCV] |  |  |  | C | ~ | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| OA-F | OUTSIDE AIR FLOW | <___> |  | <0-___ CFM> | AI |  |  | V | [ V ] | X | OA-F IS LESS THAN MINOA-F-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OUTSIDE AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
MIXED AIR TEMPERATURE CONTROL [WITH ECONOMIZER] | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T | MIXED AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT |  | [___] | <___> |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-S | ECONOMIZER STATUS | [6 empty] | V | [ V ] | X | [9 empty] | <___> | <___> | <___> | <___>
| MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO |  |  | VO | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MIXED AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
HOT DECK CONTROL | HD-T | HOT DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HD-T-SP | HOT DECK TEMPERATURE SETPOINT | <___> | [ RESET ] | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTG-OO-LL-SP | HEATING ON/OFF LOW LIMIT SETPOINT | <___> | [25%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTG-OO-HL-SP | HEATING ON/OFF HIGH LIMIT SETPOINT | <___> | [65%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| HD-V-C | HOT DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HEATING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
COLD DECK CONTROL | CD-T | COLD DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CD-T-SP | COLD DECK TEMPERATURE SETPOINT |  |  | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| CLG-OO-LL-SP | COOLING ON/OFF LOW LIMIT SETPOINT | <___> | [5%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| CLG-OO-HL-SP | COOLING ON/OFF HIGH LIMIT SETPOINT | <___> | [15%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| CD-V-C | COLD DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COOLING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE [1] TEMPERATURE CONTROL | ZN1-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN1-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-DAT | ZONE DISCHARGE AIR TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| ZN1-CD-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE COLD DECK DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| [ZN1-OCC] | ZONE OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| [ZN1-CO2] | ZONE CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN1-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE [2] TEMPERATURE CONTROL | ZN2-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN2-DAT | ZONE DISCHARGE AIR TEMPERATURE |  |  | <___> | AI | [~] |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-HD-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE HOT DECK DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| ZN2-CD-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE COLD DECK DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| [ZN1-OCC] | ZONE OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| [ZN1-CO2] | ZONE CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN1-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OTHER POINTS | RA-T | RETURN AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [ ~ ] | [ ~ ] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
[DCV: CO2 POINTS] | ZN-CO2-EFF | MAXIMUM ZONE CO2 | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-CO2 | ZONE 1 CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN1-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-CO2 | ZONE 2 CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN2-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OA-F-SP | OUTSIDE AIR FLOW SETPOINT | <___> | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MAX | MAXIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[DCV: OCC SENSOR POINTS] | OA-F-SP | OUTSIDE AIR FLOW SETPOINT | <___> | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-OCC | ZONE 1 OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-OCC | ZONE 2 OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MINOA-F-MAX | MAXIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>

## 6
NEUTRAL DECK MULTIZONE WITHOUT RETURN FAN
DESIGNER MUST MAKE BRACKETED [___] SELECTIONS AND TECHNOLOGY SELECTIONS: LONWORKS, BACNET, NIAGARA FRAMEWORK AND EITHER DELETE OR HIDE UNEEDED COLUMNS AND ROWS.
|  | COLUMN IS USED FOR BACNET (NO NIAGARA) | [12 empty] | Y | N | N | N | Y | Y | Y | N | N | Y | Y | Y | Y | Y
|  | COLUMN IS USED FOR BACNET (WITH NIAGARA) | [12 empty] | Y | N | N | Y | Y | Y | Y | N | N | N | Y | Y | N | Y
|  | COLUMN IS USED FOR LNS LONWORKS (NO NIAGARA) | [12 empty] | N | Y | Y | N | N | N | N | Y | Y | N | N | N | N | Y
|  | COLUMN IS USED FOR LONWORKS (WITH NIAGARA) | [12 empty] | N | Y | Y | Y | N | N | N | Y | Y | N | N | N | N | Y
[12 empty] | ALARMING |  |  | PRIMARY POINT INFORMATION |  |  |  | NETWORK DATA EXCHANGE |  | OVERRIDES |  |  | TREND OBJECT LOCATION (L OR R), TYPE AND INSTANCE NUMBER (PROVIDE DDC ID FOR REMOTE IN NOTES) | ALARM INFORMATION |  |  | CONFIGURATION INFORMATION
FUNCTION | NAME | DESCRIPTION | DDC HARDWARE ID | SETTING (WITH UNITS) | RANGE (WITH UNITS) | IO TYPE | HOA REQ'D | CONFIG. TYPE | M&C VIEW AND OVRD | LDP VIEW AND OVRD | TREND REQ'D | ALARM CONDITION | ALARM PRIORITY | M&C ROUTING | OBJECT TYPE AND INSTANCE NUMBER (AND PROPERTY ID) | SNVT NAME | SNVT TYPE | NIAGARA ID | DATA FROM | DATA TO | OBJECT TYPE & INSTANCE NUMBER OR COMMANDABLE | SNVT NAME | SNVT TYPE |  | ALARM TYPE (PROVIDE DDC ID FOR REMOTE IN NOTES) | NOTIFICATION CLASS OBJECT INSTANCE NUMBER | EVENT ENROLLMENT OBJECT INSTANCE NUMBER
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | <___> |  | ON/OFF | BI |  |  | V | [ V ] | [ ~ ] | SUPPLY FAN PROOF FAILED | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-LL-SP | MIXED AIR TEMPERATURE LOW LIMIT SETPOINT | <___> | [39 DEG F] | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SA-SMK | SUPPLY AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RA-SMK | RETURN AIR SMOKE | <___> |  | ALM/NORMAL | BI |  | H | ~ | ~ | ~ | ALM | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | <___> |  |  | [___] |  |  | [ ~ ][VO] | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | <___> |  | <___> | AI |  |  | V | [ ~ ] | [ ~ ] | BLDG-T IS LESS THAN BLDG-T-LL | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-T-LL | ZONE TEMPERATURE LOW LIMIT SETPOINT |  | [60 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-T-HL | ZONE TEMPERATURE LOW LIMIT SETPOINT |  | [80 DEG F] |  |  |  | C | VO | [ ~ ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | <___> |  | <___> | NET-IN |  |  | V | [ V ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| SF-SS | SUPPLY FAN START/STOP | <___> |  | ON/OFF | BO | [~] |  | VO | [ V ] | [ ~ ] | [~] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | <___> |  | <HVAC_COOL/HVAC_HEAT/HVAC_OFF> <___> | NET-OUT |  |  | [ V ] | [ ~ ] | [ ~ ] | ~ | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
SUPPLY FAN CONTROL | SF-C | SUPPLY FAN COMMAND | <___> |  | 0-100% | AO | [~] |  | VO | [V] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SF-C-MIN | SUPPLY FAN COMMAND MINIMUM |  | [50%] |  |  |  | C | VO | [~] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-SP | ZONE DAMPER COMMAND SETPOINT |  | [95%] |  |  |  | C | VO | V | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-D-C-EFF | MAXIMUM (EFFECTIVE) ZONE DAMPER COMMAND |  |  | 0-100% OPEN |  |  |  | V | V | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| SUPPLY FAN CONTROL PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
OUTSIDE AIRFLOW | MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] or [RESET PER DCV] |  |  |  | C | ~ | ~ | ~ |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| OA-F | OUTSIDE AIR FLOW | <___> |  | <0-___ CFM> | AI |  |  | V | [ V ] | X | OA-F IS LESS THAN MINOA-F-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OUTSIDE AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
MIXED AIR TEMPERATURE CONTROL [WITH ECONOMIZER] | OA-T | OUTSIDE AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T | MIXED AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT |  | [___] | <___> |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT |  | [___] |  |  |  | C | VO | [ V ] | [ ~ ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ECO-S | ECONOMIZER STATUS | [6 empty] | V | [ V ] | X | [9 empty] | <___> | <___> | <___> | <___>
| MA-D-C | MIXED AIR DAMPER COMMAND | <___> |  | 0-100% OPEN | AO |  |  | VO | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MIXED AIR DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
HOT DECK CONTROL | HD-T | HOT DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HD-T-SP | HOT DECK TEMPERATURE SETPOINT | <___> | [ RESET ] | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTG-OO-LL-SP | HEATING ON/OFF LOW LIMIT SETPOINT | <___> | [25%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| HTG-OO-HL-SP | HEATING ON/OFF HIGH LIMIT SETPOINT | <___> | [65%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| HD-V-C | HOT DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| HEATING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
COLD DECK CONTROL | CD-T | COLD DECK TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| CD-T-SP | COLD DECK TEMPERATURE SETPOINT |  |  | <___> |  |  | C | VO | [ V ] | X |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| CLG-OO-LL-SP | COOLING ON/OFF LOW LIMIT SETPOINT | <___> | [5%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| CLG-OO-HL-SP | COOLING ON/OFF HIGH LIMIT SETPOINT | <___> | [15%] | 0-100% |  |  | C | V | [11 empty] | <___> | <___> | <___> | <___> |  |  |  | <___>
| CD-V-C | COLD DECK VALVE COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ ~ ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| COOLING COIL VALVE PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
[15 empty] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE [1] TEMPERATURE CONTROL | ZN1-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN1-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-DAT | ZONE DISCHARGE AIR TEMPERATURE | <___> |  | <___> | AI | [~] |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| ZN1-CD-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE COLD DECK DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| [ZN1-OCC] | ZONE OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| [ZN1-CO2] | ZONE CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN1-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
ZONE [2] TEMPERATURE CONTROL | ZN2-T | ZONE TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ V ] | X | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-T-SP | ZONE TEMPERATURE SETPOINT |  | [OCC ADJ] | [68-77 DEG F] | AI |  | C | VO | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN2-DAT | ZONE DISCHARGE AIR TEMPERATURE |  |  | <___> | AI | [~] |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-HD-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE HOT DECK DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| ZN2-CD-D-C | ZONE DAMPER COMMAND | <___> |  | 0-100% OPEN | AO | [~] |  | VO | [ V ] | [ X ] | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZONE COLD DECK DAMPER PID LOOP SETTINGS | PROPORTIONAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | INTEGRAL CONSTANT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | BIAS | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MAXIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | MINIMUM OUTPUT | <___> | <___> |  |  |  | C | [19 empty] | <___>
|  | <____> | <___> | <___> |  |  |  | C | [19 empty] | <___>
| [ZN1-OCC] | ZONE OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| [ZN1-CO2] | ZONE CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN1-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
OTHER POINTS | RA-T | RETURN AIR TEMPERATURE | <___> |  | <___> | AI |  |  | V | [ ~ ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | <___> | ALM/NORMAL | BI |  | H | V | [ ~ ] | [ ~ ] | [ALM] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
[DCV: CO2 POINTS] | ZN-CO2-EFF | MAXIMUM ZONE CO2 | <___> |  | <___> | AI |  |  | V | [ V ] | X | [ ~ ] | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN-CO2-MAX | ZONE CO2 MAXIMUM |  | [1100 PPM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN-CO2-MIN | ZONE CO2 MINIMUM |  | [___] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-CO2 | ZONE 1 CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN1-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-CO2 | ZONE 2 CO2 | <___> | <___> | [___ PPM] | AI |  |  | V | [ V ] | [ X ] | ZN2-CO2 IS ABOVE ZN-CO2-MAX | [INFO] [CRIT] | [___] | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| OA-F-SP | OUTSIDE AIR FLOW SETPOINT | <___> | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MAX | MAXIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
[DCV: OCC SENSOR POINTS] | OA-F-SP | OUTSIDE AIR FLOW SETPOINT | <___> | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| ZN1-OCC | ZONE 1 OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| ZN2-OCC | ZONE 2 OCCUPANCY | <___> | <___> | OCC/UNOCC | AI |  |  | V | [ V ] | [ X ] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___>
| MINOA-F-MAX | MAXIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
| MINOA-F-MIN | MINIMUM OUTSIDE AIR FLOW SETPOINT |  | [____ CFM] |  |  |  | C | VO | [ V ] | [~] |  |  |  | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> | <___> |  |  |  | <___>
Notes:
|  |  | 1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS INDICATED IN THE SPECIFICATION AND IN ACCORDANCE WITH THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
|  |  | 2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
|  |  | 3) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 4) | DDC HW ID FOR DEVICE CONTAINING TREND OBJECT FOR REMOTE TRENDING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR BACNET (NO NIAGARA) |  | 5) | DDC HW ID FOR DEVICE CONTAINING EVENT ENROLLMENT OBJECT FOR REMOTE ALARMING FOR THIS SYSTEM: <___>
| THIS NOTE IS USED ONLY FOR LNS LONWORKS (NO NIAGARA) |  | 6) | DDC HW IF FOR DEVICE CONTAINING SIMPLE SCHEDULER OBJECT (OR SYSTEM SCHEDULER SEQUENCE OF OPERATIONS) FOR THIS SYSTEM: <___>