## Instructions
Multizone to Variable Volume (MZ-VV) HVAC Controls Retrofit Commissioning Guide
1. Overview
This commissioning (Cx) guide spreadsheet tool is intended to assist with the execution of a MZ-VV retrofit project to help ensure that the specified equipment has been correctly acquired, installed as required, and is functioning properly. It is designed to help the [Contracting Officer's] Quality Assurance Representative (QAR) work through project familiarization, start up, performance verification, deficiency resolution, and turnover. Each project is unique and has its own specific circumstances and requirements so this document is meant to be edited for each specific project based on the contract documents. This guide is intended to work along with the Multizone to Variable Volume Controls Retrofit Design Guide, Plans (drawings), and Procurement Package.
2. Tracker (Tab)
This tab helps the QAR track progress. It contains submittals and activities called for by the 'Specification Book' (from the appendix of the 'Design Guide'). Once completed it can serve as a quick reference index of project requirements to assist with field verification. The submittal and activity list should be edited to be project-specific based on the contract and the Contractor's submitted 'Project Schedule'. Some comments and references have been included to point the QAR towards documentation and requirements typically included in the Procurement Package. If the project includes multiple pieces of equipment of the same type you may choose to insert additional rows to accommodate each additional device or make multiple copies of the forms.
3. Start-Up Checks (Tab)
This tab lists equipment included in the project and associated start-up requirements. Specific equipment will depend on the Procurement Package and the QAR should edit the list to be project-specific. The start-up checks are intended to be used by the QAR to assist with field verification in conjunction with the contractor's start-up activities and 'Start-Up Test' report submittal. There is space to include specific references or notes to the contract specifications and drawings for ease of reference and the QAR is encouraged to complete these fields/cells. The QAR may choose to insert additional rows where there are duplicate devices such as occupancy sensors that may need to be inspected individually. The QAR should use this list to assist with on-site/field inspections primarily to help prepare for the Performance Verification Test (PVT). The project is not ready to proceed to PVT until the contractor's 'Start-Up Test' report and 'PVT Plan' are received and approved. Installation, power, and controls connections are also prerequisite to PVT.
4. Performance Verification Test (PVT) (Tab)
This tab contains a PVT template based on the sequences of operation called for by the 'Specification Book' (from the appendix of the 'Design Guide'). The PVT is the Contractor’s responsibility according to the guideline Specification Book (Appendix B of the Design Guide). The QAR should verify that PVT is a contract requirement in the Procurement Package and that the Contractor possesses the PVT Template contained in this commissioning guide and will edit the PVT template to make it project-specific and then submit it as the ‘PVT Plan’. Items are not to be removed/deleted from the template, just marked as 'not applicable' in the appropriate column. If the Contractor does not use the template, the QAR is encouraged to use it themselves during PVT, especially the tests pertaining to 'Fan Capacity Control' and 'Outdoor Air Flow Control' which are critical control functions.
5. Deficiency Log (Tab)
This is an example deficiency log that can be used to track issues, contractor communication, and resolution progress.
6. References (Tab)
This tab includes abbreviations, acronyms, definitions, and a list of resources related to a Multizone to Variable Volume Controls Retrofit.

## Tracker
Tracker - Overall Requirements for Multizone to Variable Volume (MZ-VV) Controls Retrofit
| Project/Contract Number: |  | [PO ###]
| Location (building & room number, unit identifier): |  | [Bldg123, Rm456, AHU789]
1 | Type of Multizone: |  |  | Conventional
2 | Does the multizone have a return fan? |  |  | Yes
| Submittal or Activity | Included in project? (Y/N) | Date Expected | Date Received | Status (Accepted or Rejected with Date) | Comments | Resubmitted Date | Status (Accepted or Rejected with Date) | Comments
Project Schedule
Product Data
| DDC Contractor Design Drawings | [7 empty] | e.g. Title sheet, symbols/ abbrevs, control schematic, seq of operation, points schedule.
Start-Up Test Report
PVT Plan
| PVT Start Approval | [7 empty] | Govt must provide written permission to proceed with PVT
PVT Report
| Training classroom/location | [7 empty] | Determined by QAR
| Training Attendee List | [7 empty] | Training date coordinated with Shop Supervisor
| Training | [7 empty] | Typically within 30 days of successful PVT
| Training Materials | [7 empty] | Provided at training
| VFD Start-up | [7 empty] | By Factory Representative
| VFD Start-up Form | [7 empty] | Typically submitted with "Start-Up Test Report"
| VFD training (on site) | [7 empty] | On Site, Location determined by QAR
| As-Builts (Draft) | [7 empty] | Typically prior to PVT
As-Builts (Final)
Tracker - Overall Requirements for Multizone to Variable Volume (MZ-VV) Controls Retrofit (page 2)
| Project/Contract Number: |  | [PO ###]
| Location (building & room number, unit identifier): |  | [Bldg123, Rm456, AHU789]
1 | Type of Multizone: |  |  | Conventional
2 | Does the multizone have a return fan? |  |  | Yes
| Submittal or Activity | Included in project? (Y/N) | Date Expected | Date Received | Status (Accepted/Rejected with Date) | Comments | Resubmitted Date | Status (Accepted/Rejected with Date) | Comments
Other Submittals
[Safety Plan]
[AHU Refurbishment]
[Damper Actuator Servicing]
[Insulate Ductwork]
[TAB Report]
[Other-From Project Work Statement]

## Start-Up Checks
Start-up Checks for Multizone to Variable Volume (MZ-VV) Controls Retrofit
Project/Contract Number: |  | [PO ###]
Location (building & room number, unit identifier): |  | [Bldg123, Rm456, AHU789]
Equipment | Does it apply to project? | Spec Ref. | Plans Ref. | Matches submittal? | Specific Sequence of Operation Reference | Installation location(s) | Is it installed? (Date verified) | Does it have power? (Date verified) | Is it connected to the control system (Date verified) | Communicating w/ control system? (Date verified) | Comments
Supply fan motor
Supply fan VFD
Return fan motor
Return fan VFD
Airflow measurement array
Space Sensor Modules (Thermostat) |  |  | Sensor Schedule drawing | [7 empty] | ID project-specific requirements such as Relative Humidity
Occupancy Sensors | [10 empty] | Typically occ sensors must be ceiling mount
CO2 sensors
Temperature sensors (duct)
Temperature limit switch (freeze stat)
Night Stat
Damper/Valve Actuators
Add other equipment as required by the contract

## PVT
Multizone to Variable Volume (MZ-VV) Controls Retrofit Performance Verification Test (PVT) (Template)
Project/Contract Number: |  | [PO ###]
Location (building & room number, unit identifier): |  | [Bldg123, Rm456, AHU789]
This template PVT is intended to assist the contractor. The contractor is responsible for the PVT and expected to edit this PVT to be equipment and project-specific, compliant with the contract requirements, and submitted as the ‘PVT Plan’. If a test does not apply indicate in the appropriate column. Please do not delete any rows.
Test Procedures
Submittal prepared date: |  |  | notes:
Tested By:
Test Date:
Test # | Does this test apply? | Action Item | Expected Response | Recorded Value (where applicable) | Passed (Yes/No) | Verified By | Date | Notes
Preliminary requirements
0 |  | Availability of and access to a workstation with Monitoring and Control (M&C) software or other user interface to the DDC system must be arranged in advance by contractor.
1 |  | Draft As-Builts submitted? | Draft As-Builts received by QAR | Yes / No Date Received:
2 |  | Start-Up Testing Report submitted and accepted? | Report accepted prior to PVT | Yes / No Date Accepted: |  |  |  | Report certifies system is installed and functioning as required and is ready for PVT
3 |  | Test & Balance (TAB) Report (if required) submitted and accepted? | Report accepted prior to PVT | Yes / No Date Accepted:
4 |  | Written permission to start PVT has been provided by the Government/QAR? | Permission to start has been provided | Yes / No Date Received:
Graphics - Monitoring and Control (M&C) Software Configuration and System Displays - as applicable
This test pertains to UMCS front-end M&C software functionality. Applicability of the individual tests should be checked against the contract requirements.
5 |  | Displayed Points: Verify that all points requiring M&C Display (as specified or shown on the Points Schedule drawing) are included in the system graphics. | All required points are shown on the system graphics.
6 |  | Point Settings: Verify that all setpoints, limits, and operator configurable point settings as specified (e.g. in sequence of operation) or shown on the Points Schedule drawing are entered into the DDC System | All setpoints, limits, and operator configurable settings have been entered into the DDC System
7 |  | Overrides: Verify that all points specified or shown as requiring M&C Overrides are included on the system graphics as override points. | All required points are overridable via the system graphics.
8 |  | Overrides: Verify that a sampling (up to 25%) of overrides of the Gov't choice actually override the indicated points, and that the override can be released from the system graphics display. | All tested overrides function properly - the point can be overridden and then released. | List points tested:
9 |  | Alarms: Verify that all alarms required by the Points Schedule are configured as indicated. | All alarms required by the Points Schedule are configured.
10 |  | Trends: Verfiy that all trends as specified or required by the Points Schedule are configured and values are being trended. | All required trends are configured and trending values.
Local Display Panel (LDP) Configuration - if applicable
11 |  | Verify that all points shown on the Points Schedule as requiring LDP display or override are properly configured to display or provide override. | Display and overrides are provided in accordance with Points Schedule.
Sensor Accuracy (see reference tab for acronyms)
12 |  | One point accuracy check for up to three sensors of each type of the government's choosing. | Each sensor exhibits accuracy to the specified requirement. | (List sensors checked and readings)
13 |  | Command the CD valve to closed | CD-T should be about the same as MA-T after the temperatures stabilize. Record the temperatures. | Cold Deck Temp ___________________ Mixed Air Temp ____________________ Actual valve position: ________________ |  |  |  | Expect CD-T to be slightly higher than MA-T due to heat rise across the fan.
14 |  | Command the HD valve to closed (mark this step as N/A for HD Bypass unit which has no HD valve) | HD-T should be about the same as MA-T after the temperatrues stabilize. Record the temperatures. | Hot Deck Temp ____________________ Mixed Air Temp ____________________ Actual valve position: ________________ |  |  |  | Expect HD-T to be slightly higher than MA-T due to heat rise across the fan.
15 |  | Command each zone valve to closed (for HD Bypass system only) (mark as N/A if the unit has no zone heating valves) | ZN-DA-T should be about the same as average of CD-T and MA-T after the temperatures stabilize. Record the temperatures. | Mixed Air Temp ____________________ Cold Deck Temp ____________________ Zone Temps: ______________________
16 |  | Command the OA-D to full open | MA-T should be about the same as OA-T after the temperatures stabilize. Record the temperatures. | Mixed Air Temp ____________________ Outside Air Temp ___________________ Actual damper position: ______________
17 |  | Command the OA-D to full closed | MA-T should be about the same as RA-T after the temperatures stabilize. Record the temperatures. | Mixed Air Temp _____________________ Return Air Temp ____________________ Actual damper position: ______________
18 |  | For each room with occ sensor, create motion outside doorway and monitor occupancy sensor. (Note: Result will need to be checked at the control system used to monitor the sensor.) | Occ sensors do not ‘see’ beyond the doorway. | List each room/occ sensor and result:
19 |  | For each room with occ sensor, create motion at remote points in the room. (Note: If occupancy sensor does not have visual indication of sensing motion the control system may be used to monitor the sensor.) | Occ sensor senses motion throughout the entire room. | List each room/occ sensor and result:
20 |  | For up to 3 occupancy sensors of the Government's choosing, visually verify the off-delay time (time-out) settings at the sensor. | Verify settings are in accordance with the specifications. | List 3 sensors and observed response:
Supply Fan VFD Basic Operation
21 |  | From the Supply Fan VFD, turn the H-O-A switch to Off | The VFD should stop the fan.
22 |  | From the Supply Fan VFD, turn the H-O-A switch to Hand | The VFD will start the fan and slowly ramp it up to speed
Optional (if specified): An Alarm will be generated through the BAS for Hand Position
23 |  | From the Supply Fan VFD, adjust the frequency reference to 75% (45Hz) | The VFD will drive the fan to the reference frequency
|  | From the Supply Fan VFD, adjust the frequency reference to 1%. Once fan speed reaches a minimum record minimum fan speed. | Fan speed ramps down to the specified minimum fan speed typically between 35% to 50% but check specified minimum.
24 |  | From the Supply Fan VFD, turn the H-O-A switch to auto | The VFD will return to automatic control, and operate according to the fan capacity control loop according to a subsquent test.
25 |  | Simulate restart from power loss | Power down VFD at disconnect, then reenergize disconnect after one minute and confirm VFD and fan start and control to setpoint.
26 |  | Reset all alarms
Occ / Unocc / Warm-up&Cool-Down --- Mode Control
27 |  | Verify UNOCCUPIED MODE conditions: From the DDC system display place the system into Occupied mode (if not already in Occupied). After a short delay (appx 1-2 minutes) place the system into Unoccupied Mode. | SF (and RF, as applicable) stop | Observed Fan response:
|  |  | The chilled water valve will close to the coil. | Observed Chilled Water Valve position:
|  |  | The heating water valve(s) will close to the coil. | Observed Heating Water Valve position:
|  |  | The outside air dampers will close. | Observed Outside Air Damper position:
|  |  | The exhaust air damper will close. | Observed Exhaust Air Damper position:
|  |  | The return air damper will open 100%. | Observed Return Air Damper position:
28 |  | Verify OCCUPIED MODE conditions: From the DDC system display place the system into Unoccupied mode (if not already in Unoccupied). After a short delay (appx 1-2 minutes) place the system into Occupied Mode. | SF (and RF, as applicable) start | Observed Fan response:
VFD ramps the SF (and RF) up to speed.
|  |  | The outdoor air flow displayed by the DDC equals the outdoor airflow setpoint (after airflows come up to speed). | Outdoor airflow CFM setpoint: Outdoor airflow CFM:
|  |  | Cold Deck control valve modulates to maintain CD-T-SP. The commanded positions of the zone dampers/valves may need to be overridden to enable modulation of the CD valve. | Observed CD valve response:
|  |  | Hot Deck control valve modulates to maintain HD-T-SP. The commanded positions of the zone dampers/valves may need to be overridden to enable modulation of the HD valve. | Observed HD valve response:
Economizer is a subsequent test.
29 |  | Verify WARM-UP / COOL DOWN MODE. Verify DDC system is configured for these modes and the day/time settings are configured. | DDC is programmed/configured and the days/times are set as specified/shown. | Record Warm-up Cool Down days/times:
27 |  | WARM-UP MODE. Place/override system into WARM-UP mode. | All control loops are enabled and functioning except the OA control loop damper should be closed. | Observed OA damper position:
28 |  | COOL DOWN MODE. Place/override system into COOL DOWN mode. | All control loops are enabled and functioning except the OA control loop damper should be closed. | Observed OA damper position:
Occupancy Modes (make sure all deadbands are 5 Deg F or less for this test):
30 |  | From the DDC system display, override the time schedule for unoccupied to be current time plus 2 minutes. | After 2 minutes the system goes to Unoccupied mode. | Observations:
The supply fan should stop
Return Air Damper should open
Unit Outside Air Damper should close
Water valves close.
31 |  | From the DDC system display, adjust the night setback High-limit (HL) temperature setpoint to be the current space temperature minus 6 degree F. | Fan Capacity loop enables. | Observations:
Econ loop enables
Cold Deck control loop is enabled
Zone temp control loop is enabled.
32 |  | From the DDC system display, adjust the night setback temperature setpoint to be the current space temperature plus 1 degF. | Fan Capacity loop is disabled. Unit returns to Unocc mode. | Observations:
Econ loop is disabled. Unit in Unocc mode.
Cold Deck control loop is disabled. Unit in Unocc mode.
Hot Deck control loop does not enable.
Zone temp control loop is diaabled. Unit in Unocc mode.
33 |  | From the DDC system display, adjust the night setback Low-limit (LL) temperature setpoint to be the current temperature plus 6 deg F. | Fan Capacity loop enables. | Observations:
Zone Temp loop enables.
[Hot Deck control loop is enabled]
34 |  | From the DDC system display, adjust the night setback temperature setpoint to be the current space temperature plus 2 degF. | Fan Capacity loop is disabled. Unit returns to Unocc mode. | Observations:
Econ loop is disabled. Unit in Unocc mode.
Cold Deck control loop is disabled. Unit in Unocc mode.
[Hot Deck control loop does not enable.]
Zone temp control loop is disabled. Unit in Unocc mode.
35 |  | Release all overrides. | System will return to normal control.
Fan Capacity Control
This test verifies that the supply fan (and RF as applicable) speeds up and slows down based on the commanded position of the zone heating/cooling dampers (and the zone control valves in a ‘Bypass MZ’ unit). When any zone is calling for more than 95% or less than 5% heating or cooling (based on zone damper or zone valve commanded positions) the fan speed should speed up because of the increased heating/cooling demand, otherwise the fan tends to slow down. Refer to the ‘Sequence of Operation’ and the ‘Control Logic Diagram’ drawing.
36 |  | From DDC system display place the system in occupied mode.
37 |  | Override all zone dampers (and zone control valves, as applicable) to 20% or otherwise create conditions where no zone damper (or zone valve) is above 95% or below 5% commanded open position. | Fan speed is less than 100% and is decreasing or stable at less than 100%. | Observed fan performance/speed: |  |  |  | Note: Hot Deck Bypass MZ will have zone heating control valves.
38 |  | Verify that the RF speed is tracking SF speed as required. | A various speeds, the RF speed is observed to be a constant OFFSET (amount) less than the SF speed | SF speed: ____ ____ ____ ____ RF speed: ____ ____ ____ ____
39 |  | Override one zone damper to 94% -For a 'Neutral Deck MZ' override a cold deck zone damper to 94% | Fan speed remains at less than 100% and is decreasing or stable at less than 100%. | Observed fan performance:
40 |  | Override the same zone damper to 96% | Fan speed begins to increase. | Observed fan performance: |  |  |  | Once it is verified that fan speed is increasing, the rate of change can be increased by setting the zone damper to a more open position, e.g. 100%
41 |  | Override the same damper to 20%. Note: All zone dampers (and valves) should be overridden to 50%. | Fan speed begins to decrease. | Observed fan performance:
42 |  | Override the same damper to 4%, except: -For a 'Neutral Deck MZ' override a hot deck zone damper to 4% -For 'Hot Deck Bypass MZ' override a zone valve to 4% | Fan speed begins to increase. | Observed fan performance:
43 |  | Override same damper or valve (as in previous step) to 2% | Fan speed continues to increase. | Observed fan performance:
44 |  | Override the same damper or valve (as in previous step) to 20% in preparation for the next test.
Cold Deck enable/disable
This test verifies that the Cold Deck cooling coil control valve is enabled (to modulate), then is disabled (i.e. closed) when there is little to no call for cooling in any zone. Refer to the ‘Sequence of Operation’ and the sequencing diagram(s) in the ‘Control Logic Diagram’ drawing.
45 |  | From DDC system display Place the system in occupied mode.
46 |  | Cold Deck test steps: 'Override all zone dampers to 20% or otherwise create conditions where all zone dampers are above 5% commanded/ override open position. -For a 'Neutral Deck MZ' override all cold deck zone dampers to 20% (not the hot deck zone dampers) | Cold deck cooling coil control valve is enabled to perform modulating control | Observed state of cold deck control valve:
47 |  | Override all zone dampers to less than 5%. -For a 'Neutral Deck MZ' override all cold deck zone dampers to less than 5% (not the hot deck zone dampers) | Cold deck cooling coil control valve is disabled and closed | Observed state of cold deck control valve:
48 |  | Override one zone damper to greater than 15%. -For a 'Neutral Deck MZ' override one cold deck zone damper to greater than 15% (Not a hot deck zone damper) | Cold deck cooling coil control valve is enabled to perform modulating control | Observed state of cold deck control valve:
49 |  | Release all overrides or proceed to the next test
Hot Deck enable/disable (does not apply to 'Hot Deck Bypass' MZ)
This test verifies that the Hot Deck heating coil control valve is enabled (to modulate), then is disabled (i.e. closed) when there is little to no call for heating in any zone. Refer to the ‘Sequence of Operation’ and the sequencing diagram(s) in the ‘Control Logic Diagram’ drawing.
50 |  | From DDC system display Place the system in occupied mode.
51 |  | Hot Deck test steps: 'Override all zone dampers to less than 25% or otherwise create conditions where all zone dampers are less than 25% commanded/ override open position. -For a 'Neutral Deck MZ' override all hot deck zone dampers to less than 25% (not the cold deck zone dampers) | Hot deck control valve is enabled to perform modulating control | Observed state of hot deck control valve:
52 |  | Override all zone dampers to greater than 65%. -For a 'Neutral Deck MZ' override all hot deck zone dampers to greater than 65% (Not the cold deck zone dampers) | Hot deck heating coil control valve is disabled and closed | Observed state of hot deck control valve:
53 |  | Override one zone damper to less than 25%. -For a 'Neutral Deck MZ' override one cold deck zone damper to less than 25% (not a hot deck zone damper) | Hot deck heating coil control valve is enabled to perform modulating control | Observed state of hot deck control valve:
54 |  | Release all overrides
Outside Air Flow Control - Fixed Flow Setpoint (verify that this sequence of operation is the one that is specified)
This test verifies that the OA flow setpoint can be maintained and that the OA flow setpoint is maintained even if the mixed air economizer tries to move the OA damper to the closed position.
55 |  | From DDC system display Place the system in occupied mode.
56 |  | Override supply fan speed to 100% | Verify that the outside air (OA) flow cfm setpoint is achieved and maintained | Observed conditions: -OA flow setpoint (cfm): -OA air flow value (cfm): -Fan speed:
57 |  | From DDC system display, increase or decrease OA Flow setpoint by about 20% | Mixed air dampers modulate to adjust to the change in outside air (OA) flow cfm setpoint | Observed conditions: -OA flow setpoint (cfm): -OA air flow value (cfm): -Fan speed:
58 |  | Enable the economizer. Override the MA-T setpoint to 100 degF (or a setting well above the OA-T). | The OA damper should not close below that needed to maintain the OA flow setpoint | Observed conditions: -OA damper command: -OA flow setpoint (cfm): -OA air flow value (cfm): -Fan speed:
59 |  | Release all overrides: fan speed, OA airflow setpoint, econ enable, MA-T-SP
Outside Air Flow Control - Occupancy Sensor - Demand controlled ventilation (verify that this is required by the specified sequence of operation)
This test verifies that the OA flow setpoint can be maintained. It also verifies that the OA flow setpoint adjusts based on zone occupied/unoccupied sensor signals as specified. The test is performed by overriding the occupancy sensor signals and observing the change in OA flow cfm setpoint. The test also verifies that the OA flow setpoint is maintained even if the mixed air economizer tries to move the OA damper to the closed position.
60 |  | From DDC system display Place the system in occupied mode.
61 |  | Override supply fan speed to 100% and verify that the outside air (OA) flow setpoint displayed at the DDC system display is achieved and maintained. | OA flow cfm setpoint is achieved and maintained. | Observed conditions: -OA flow setpoint (cfm): -OA air flow value (cfm): -Fan speed:
62 |  | Override all occupancy sensors to 'UNOCCUPIED' and verify that the OA flow setpoint adjusts to the specified value. | The OA flow cfm setpoint adjusts to the specified UNOCCUPIED value. | Observed conditions: -Specified OA flow setpoint (cfm): -Displayed OA flow setpoint (cfm):
63 |  | Override all occupancy sensors to 'OCCUPIED' and verify that the OA flow setpoint adjusts to the specified value. | The OA flow cfm setpoint adjusts to the specified OCCUPIED value. | Observed conditions: -Specified OA flow setpoint (cfm): -Displayed OA flow setpoint (cfm):
64 |  | Enable the economizer. Override the MA-T setpoint to 100 degF (or a setting well above the OA-T). | The OA damper should not close below that needed to maintain the OA flow setpoint | Observed conditions: -OA damper command: -OA flow setpoint (cfm): -OA air flow value (cfm): -Fan speed:
65 |  | Release all overrides: fan speed, occupancy sensors, economizer enable, MA-T-SP
Outside Air Flow Control - CO2 Sensor - Demand controlled ventilation (verify that this is required by the specified sequence of operation)
This test verifies that the OA flow setpoint can be maintained. It also verifies that the OA flow setpoint adjusts based on zone CO2 sensor signals as specified. The test is performed by overriding the CO2 sensor (ppm) signals and observing the change in OA flow cfm setpoint.
66 |  | From DDC system display Place the system in occupied mode.
67 |  | Override supply fan speed to 100% and verify that the outside air (OA) flow setpoint is achieved and maintained. | OA flow cfm setpoint is achieved and maintained. | Observed conditions: -OA flow setpoint (cfm): -OA flow value (cfm): -Fan speed:
68 |  | Record all zone CO2 values and verify that OA flow setpoint is correct based on the maximum CO2 value. | The OA flow cfm setpoint is correct as specfifed based on the maximum zone CO2 value. | Observed conditions: -Record all zone CO2 ppm values: -Maximum zone CO2 ppm value: -OA flow setpoint (cfm): |  |  |  | Note: You may have to linearly interpolate to determine the cfm setpoint based on specifed CO2 range (Google: "linear interpolation calculator").
69 |  | Override one CO2 value to the maximum specified value shown in the "Reset Schedule". | Verify that the outside air (OA) flow cfm setpoint adjusts to the upper specified value based on the overidden CO2 value. | Observed conditions: -Specified upper CO2 value (ppm): -Specified upper OA flow setpoint (cfm): -Displayed override CO2 value (ppm): -Displayed OA flow setpoint (cfm):
70 |  | Override all CO2 values to the minimum specified value shown in the "Reset Schedule". | Verify that the outside air (OA) flow cfm setpoint adjusts to the lower specified value based on the overidden CO2 values. | Observed conditions: -Specified lower CO2 value (ppm): -Specified lower OA flow setpoint (cfm): -Displayed override CO2 value (ppm): -Displayed OA flow setpoint (cfm):
71 |  | Enable the economizer. Override the MA-T setpoint to 100 degF (or a setting well above the OA-T). | The OA damper should not close below that needed to maintain the OA flow setpoint | Observed conditions: -OA damper command: -OA flow setpoint (cfm): -OA air flow value (cfm): -Fan speed:
72 |  | Release all overrides: fan speed, CO2 sensors, econ enable, MA-T-SP
Zone Temperature Control
73 |  | Increase the space zone sensor setpoint to at least 3 degF above the current space temperature. | -Hot deck damper modulates more open. -For Hot Deck BP MZ: zone heating control valve modulates towards open. | 'Observed conditions:
|  |  | Cold deck damper modulates more closed. | 'Observed conditions:
74 |  | Decrease the space zone sensor setpoint to at least 3 degF below the current space temperature. | -Hot deck damper modulates more closed. -For Hot Deck BP MZ: zone heating control valve modulates towards closed. | 'Observed conditions:
|  |  | Cold deck damper modulates more open. | 'Observed conditions:
Economizer Control (Be careful not to freeze chilled water coil if test during winter)
75 |  | From the DDC system display, override the MA-T-HL setpoint to be 4 degF more than current OA-T, and override the MA-T-LL setpoint to be 4 degF less than current OA-T. Set the MA-T sepoint to be the midpoint temperature between MA-T-LL and MA-T-HL. (and deadband remains 2 degF) | The Econ mode is enabled. | 'Observed conditions:
|  |  | The outside air, relief, and return dampers modulate to maintain the new (current) MAT setpoint. | 'Observed conditions:
76 |  | From the DDC system display, override the MA-T-HL setpoint to be 2 degF more than current OA-T, and override the MA-T-LL setpoint to be 2 degF less than current OA-T. Maintain the MA-T sepoint to be the midpoint temperature between MA-T-LL and MA-T-HL. (and deadband remains 2 degF) | The Econ mode is disabled. | 'Observed conditions:
|  |  | The outside air and relief air dampers are controlled by the Outside Air Flow Control loop. | 'Observed conditions:
77 |  | Release all Overrides. | System will return to normal operation.
Pre-Emptive Freeze Protection
This test verifies that the OA damper moves towards closed as the mixed air temperature (MA-T) gets cold and threatens to trip the MA-T-LL device (freeze stat).
78 |  | From DDC system display place the system in occupied mode and disable the economizer. | The OA damper(s) are under control of the OA flow control loop. | Observed conditions:
79 |  | Adjust the MA-T-LL-SP to be 3 degrees F above the current MA-T value. | The OA damper is open (at least partially) and modulating under control of the OA Flow Control loop | Observed conditions:
80 |  | Adjust the MA-T-LL-SP to be 8 degrees F above the current MA-T value. | The OA damper is closed | Observed conditions:
81 |  | Re-enable the economizer
Safeties and Alarms - as applicable
82 |  | With the System in occupied mode, turn the supply fan VFD H-O-A to the 'off' position. | -The fan(s) stop. -A fan failure alarm will be issued (at the UMCS front-end, as applicable) | Observed performance:
83 |  | Return the H-O-A switch to the auto position.
84 |  | With the fan running, immerse a 1-foot length of the mixed-air LL (freeze stat) sensor in ice. | -The fan(s) stop. -Outside air dampers close. -A low limit alarm is generated (at the UMCS front-end, as applicable). -optional: HD and CD valves open 100% | Observed performance:
85 |  | Reset the mixed-air LL manual switch and reset button. | -The fan(s) start -Alarm clears (at the UMCS front-end, as applicable). | Observed performance:
86 |  | Simulate a duct detector unit shutdown by tripping the return duct detector (one method: use a magnet per manufacturer instructions). | AHU fans and all control modes are disabled. | Observed performance: |  |  |  | Note: You should notify the fire department of this planned test.
87 |  | With the system in alarm, turn the H-O-A switch for the VFD's to the hand position and back to auto. | The VFD's will remain off. | Observed performance:
88 |  | Press the reset button to reset the duct detector and clear the alarms (at the UMCS front-end, as applicable). | The alarms will clear and the system will return to automatic. | Observed performance:
Other tests as needed to verify compliance with the sequence of operation and other contract documents
Endurance Test
This test creates a trend log(s) to monitor and record system performance for a [1-week] period. The primary intent is to verify that: --The fan speed adjusts as the zones adjust their call for heating and cooling (as the zone control dampers/valves change), --The OA flow requirement is met
89 |  | Create a trend log(s) to monitor and record system performance for 1 week (or as specified) including all points as specified but otherwise minimally consisting of: fan speed, all zones damper/valve commands, all zone occupancy sensors status, all zone CO2 sensor values, OA/MA damper commands, OA flow setpoint, OA flow. | Trend logs demonstrate that the system performance is acceptable and according to the sequence of operation and specifications. | List and briefly describe trend logs/graphs at the end of the endurance test period:
Other
90 |  | At the Governments request demonstrate compliance with any contract requirement that was not demonstrated in a test defined above. | Contract requirement is met.

## Deficiency Log
Deficiency Log
Project/Contract Number: |  | [PO ###]
Location (building & room number, unit identifier): |  | [Bldg123, Rm456, AHU789]
Item # | Date | Observed Deficiency | Contractor Response | Resolution | Resolved Date
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15

## References
Abbreviations, Acronyms, Definitions, Resources
AFMA | Air Flow Measurement Array
AHU | Air Handling Unit
Bypass (hot-deck bypass) | Hot-Deck Bypass is a type of multizone system
CC | Cooling Coil
CD | Cold Deck
cfm | cubic feet per minute
Configurable point | A control value or setting usually set during installation using a special software (engineering, configuration, or programming software) tool and which is seldom changed
Conventional (conv) | Conventional Multizone a type of multizone system
CV | Constant (Air) Volume
Cx | Commissioning
D | Damper
DCV | Demand-Controlled Ventilation
DDC | Direct Digital Control
Econ | Economizer
front-end | a computer workstation or user interface, typically a UMCS with M&C software
HC | Heating Coil
HD | Hot Deck
HL | High Limit
H-O-A | Hand-Off-Auto(matic) A 3-position switch.
HVAC | Heating, Ventilation, and Air Conditioning
HW | Hot Water or Hardware
LL | Low limit
LDP | Local Display Panel. A small user interface typically located in a mechanical room.
MA | Mixed Air
M&C | Monitoring and Control -- UMCS front-end software that provides a user interface and perfoms supervisory functions such as alarm handling, scheduling, and trend data logging.
MZ | Multizone
Neutral Deck | Neutral Deck is a type of multizone system
OA | Outside Air
OA-D | Outside Air Damper
Occ | Occupied or occupancy
Operator configurable point | Same as a 'Configurable point' except it is accessible by a user/operator through a user interface such as M&C software with a graphics display or an LDP
Override | Changing a point (value or setting) outside of the normal sequence of operation. Overrides are typically used by an operator and generally originate at a user interface.
PVT | Performance Verification Test
PWS | Performance Work Statement
QAR | Quality Assurance Representative. This is intended to be a government employee.
RA | Return Air
RF | Return Fan
RH | Relative Humidity
SA | Supply Air
SF | Supply Fan
SOO | Sequence of Operation
SP | Set point
T | Temperature
TAB | Test, adjust, balance
UMCS | Utility Monitoring and Control System. Consists of a front-end (workstation) with M&C software along with (typically) multiple underlying DDC systems.
User Interface | Provides user/operator access through an interface such as M&C software with a graphics display or an LDP
VFD | Variable Frequency Drive
VV | Variable volume
Resources:
Environmental Security Technology Certification Program (ESTCP) technology transfer project EW19-5026,
'Multizone to Variable Volume Controls Retrofit':
--Design Guide (recommendations, specifications, sequences of operation, PWS)
--Drawings Templates
--Points Schedule
--Technical Note
--ESTCP Technology Fact Sheet
--Field Scoping Guide
--Retrofit Savings Estimator

## menu options
MZ Types: | Return Fan:
Conventional | Yes
Neutral Deck | No
Hot Deck Bypass