TABLE 4-8. SAC/YOUTH/TEEN TOILETS

|  |  |
| --- | --- |
| **Description/ Usage** | See Table 3-1 for Service specific toilet requirements. Separate toilets for male and female youth. These toilets are not for use by adults.  Navy Youth toilets are shared with the SAC youth, but not the teens while the center is occupied by pre-teens—see Table 4-9 for Navy Teen (unisex) toilet criteria. |
| **Min. Ceiling Ht.** | 2.44 m (8 ft.) minimum. |
| **Finishes** | **Walls.**  Epoxy or enamel painted, moisture-resistant gypsum wallboard with a ceramic tile wainscot. Provide full-height ceramic tile on wet walls; consider full-height ceramic tile on all walls. |
|  | **Floor.** Ceramic tile. |
|  | **Ceiling.** Painted, moisture-resistant gypsum board. |
| **Plumbing** | Provide water closets, urinals, and lavatories based on the applicable code for the calculated occupancy. To prevent scalding of youth, limit water temperature to 43 C (110 F). Provide a floor drain. Provide a keyed hose bibb. Consider providing a drinking fountain outside this room. Provide wall-hung water closets and urinals.   The Navy requires floor-mounted urinals. |
| **HVAC** | 20 C (68 F) minimum, 26 C (78 F) maximum. Provide at minimum 4 – 6 air changes per hour. Ventilate to the exterior per code. |
| **Fire Protection** | Provide system per paragraph 3-5.3. |
| **Power** | Provide outlets per code. |
| **Lighting** | 540 lux (50 fc). |
| **Communication** | **CCTV.** None required.  **CATV/Internal Video.** None required.  **PA/Audio.** None required.  **Telephone.** None required.  **Data.**  None required.  **Security.** Ensure entrance can be audibly and visually monitored from Check-in. |
| **Casework** | Solid-surface countertop supported at both ends with either underhung or integral sink.  Phenolic or solid composite toilet and urinal partitions secured at floor and ceiling. |
| **Furnishings Fixtures & Equipment (FF&E)** | Toilet accessories: toilet paper dispensers, paper towel dispenser with integrated trash receptacle, robe hooks, grab bars, and soap dispensers.  Mirror. |
| **Special Requirements** |  |
| For use during project execution by the appropriate Service agency | |
| **Occupancy** | Staff. |
|  | Patrons/Youth. |
| **Min. net m2 (ft2)** |  |