## Instructions (MS Word)
Notes to Designer:
| 1 | These instructions are an embedded Word file and thus are not shown in full in Excel. The first page is shown here but to access the complete instructions double-click on the text to edit the Word file
| 2 | Include these instructions on the 'Points Schedule Instructions' drawing sheet. Include the complete instructions (including the 25 10 10 contractor instructions). To convert the text to ALL CAPS for inclusion on the drawing: double-click to edit the text, from the Edit menu choose Select All then from the Format menu choose Font and check the box labeled All Caps.)

## Index
Worksheet | Description
3 | ALL AIR SMALL PACKAGE UNITARY SYSTEM
4 | HEATING AND VENTILATING UNIT
5 | SINGLE ZONE WITH HEATING AND DX COILS
6 | SINGLE ZONE WITH HEATING AND COOLING COILS
7 | SINGLE ZONE WITH DUAL TEMPERATURE COIL
8 | SINGLE ZONE WITH HEATING AND COOLING COILS AND RETURN AIR BYPASS
9 | SINGLE ZONE WITH HUMIDITY CONTROL
10 | DUAL DUCT WITH RETURN FAN
11 | MULTIZONE WITH RETURN FAN
12 | MULTIZONE WITH HOT DECK BYPASS AND RETURN FAN
13 | VAV WITH RETURN FAN
14 | TERMINAL AND ZONE UNITS
15 | HYDRONIC HEATING HOT WATER FROM DISTRIBUTED STEAM CONVERTER
16 | HIGH TEMPERATURE HOT WATER/HOT WATER HEAT EXCHANGER
17 | HOT WATER BOILER WITH CONSTANT AND NON-CONSTANT BOILER LOOP
18 | STEAM/HOT WATER CONVERTER DUAL TEMPERATURE SYSTEM
19 | HTHW/HOT WATER HEAT EXCHANGER DUAL TEMPERATURE SYSTEM
20 | SECONDARY HYDRONIC WITH CONSTANT SPEED PUMPING
21 | SECONDARY HYDRONIC WITH VARIABLE SPEED PUMPING

## 3
ALL AIR SMALL PACKAGE UNITARY SYSTEM
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES |  | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES) | <___> | ALM/NORMAL | <___> | <BI> | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RST-BUT | SYSTEM RESET BUTTON | ~ | ~ | <___> | [___] | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [___] | [___] | <___> | <___> | ~ | ~ | ~
START/STOP | <___> | HEAT-OFF-COOL SWITCH INPUT | ~ | HEAT/OFF/COOL/ <EMERG> | <___> | <___> | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | <___> | <___> | NVI | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | ~ | OCC/UNOCC | <___> | BI | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| SF-ON/AUTO | SUPPLY FAN ON/AUTO SWITCH | ~ | ON/AUTO | <___> | BI | ~ | ~ | [ ~ ] | [ ~ ] | <___> | <___> | ~ | [ ~ ] | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (SEE NOTES) | ~ | HVAC_COOL/ HVAC_HEAT/ HVAC_OFF | <___> | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T MORE THAN 77 DEG F OR BELOW 68 DEG F | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | OCCUPANT ADJUSTABLE | [68-77 DEG F] | <___> | AI | ~ | [ ~ ] | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-T-SP-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCC MODE |  |  | <___> |  | ~
| SF-SS | SUPPLY FAN START/STOP COMMAND | ~ | ON/OFF | <___> | BO | [~] | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| COMP-CLG/HTG | COMPRESSOR (PKG UNIT) COOLING/HEATING MODE | ~ | CLG/HTG | <___> | BO | [~] | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| COMP-SS | COMPRESSOR (PKG UNIT) START/STOP | ~ | ON/OFF | <___> | BO | [~] | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| EMERG-HTG-2P | EMERG HEATING COMMAND (2-POS) | ~ | ON/OFF | <___> | AO | [~] | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | HEATING COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | COOLING COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 4
HEATING AND VENTILATING UNIT (UNIT VENTILATOR)
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY | [5 empty] | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE |  | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D | [5 empty] | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | HTG-DA-T-LL | HEATING COIL DISCHARGE TEMPERATURE LOW LIMIT SWITCH | [39 DEG F] | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ |  | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| SA-SMK | SUPPLY AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ |  | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RA-SMK | RETURN AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ |  | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | ~ | ~ | <___> | [___] | ~ | ~ | ~ | ~ | ~ | ~ |  | ~ | [___] | <___> | <___> | ~ | ~ | ~
| SF-S | SUPPLY FAN STATUS |  | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> |  | ~ | ~ | ~ | ~ | SUPPLY FAN PROOF FAILED | [info] [crit] | [___]
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P |  | ~ | ~ | ~ | ~ | BLDG-T IS LESS THAN BLDG-T-LL | [info] [crit] | [___]
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT | [55 DEG F] | ~ | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> |  | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | <___> | <___> | NVI | ~ | [ X ] | X | [ ~ ] | <___> | <___> |  | SEE NOTES |  |  |  | ~ | ~ | ~
| SF-SS | SUPPLY FAN START/STOP | ~ | ON/OFF | <___> | BO | [~] | [ X ] | X | [ ~ ] | <___> | <___> |  | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | ~ | HVAC_HEAT/ HVAC_OFF | <___> | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS |  | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P |  | ~ | ~ | ~ | ~ | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | [OCC ADJ] | [68-77 DEG F] | <___> | AI | ~ | [ X ] | X | X | <___> | <___> |  | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| HTG-V-C | HEATING COIL VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> |  | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| OA-D-C | OUTSIDE AIR DAMPER COMMAND | ~ | <0-100% OPEN> | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> |  | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| OA-D-MIN | OUTSIDE AIR DAMPER MINIMUM POSITION | [ ___ CFM] | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | HEATING COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | OUTSIDE AIR DAMPER PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | SA-T | SUPPLY AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> |  | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | ALM/NORMAL | <___> | BI | ~ | [ ~ ] | [ ~ ] | ~ | <___> | <___> |  | ~ | ~ | ~ | ~ | [ALM] | [info] [crit] | [___]
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 5
SINGLE ZONE WITH HEATING AND DX COILS
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS |  | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | SUPPLY FAN PROOF FAILED | [info] [crit] | [___]
| HTG-DA-T-LL | HEATING COIL DISCHARGE TEMPERATURE LOW LIMIT SWITCH | [39 DEG F] | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| SA-SMK | SUPPLY AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RA-SMK | RETURN AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | ~ | ~ | <___> | [___] | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [___] | <___> | <___> | ~ | ~ | ~
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | BLDG-T IS LESS THAN BLDG-T-LL | [info] [crit] | [___]
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT | [55 DEG F] | ~ | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | <___> | <___> | NVI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| SF-SS | SUPPLY FAN START/STOP | ~ | ON/OFF | <___> | BO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | ~ | HVAC_HEAT/ HVAC_OFF | <___> | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | ~ | OPEN/CLOSED | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | MINIMUM OUTSIDE AIR FLOW SETTING | [____ CFM] | ~ | <___> |  | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE TEMPERATURE CONTROL: MA DAMPERS HEATING COIL DX COIL | OA-T | OUTSIDE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| MA-D-C | MIXED AIR DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT | [___] | ~ | <___> |  | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ X ] | X | <___> | <___> | ~ | ~ | ~
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT | [___] | ~ | <___> |  | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ X ] | X | <___> | <___> | ~ | ~ | ~
|  | MIXED AIR PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
| ZN-T | ZONE TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | [OCC ADJ] | [68-77 DEG F] | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ X ] | X | <___> | <___> | ~ | ~ | ~
| HTG-V-C | HEATING COIL VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| DX-V-C | DX UNIT COMMAND | ~ | <___> | <___> | <___> | ~ | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | HEATING COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | DX UNIT PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | SA-T | SUPPLY AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | ALM/NORMAL | <___> | BI | ~ | [ ~ ] | [ ~ ] | ~ | <___> | <___> | ~ | ~ | ~ | ~ | [ALM] | [info] [crit] | [___]
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 6
SINGLE ZONE WITH HEATING AND COOLING COILS
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | ~ | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | SUPPLY FAN PROOF FAILED | [info] [crit] | [___]
| HTG-DA-T-LL | HEATING COIL DISCHARGE TEMPERATURE LOW LIMIT SWITCH | [39 DEG F] | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| SA-SMK | SUPPLY AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RA-SMK | RETURN AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | ~ | ~ | <___> | [___] | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [___] | <___> | <___> | ~ | ~ | ~
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | BLDG-T IS LESS THAN BLDG-T-LL | [info] [crit] | [___]
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT | [55 DEG F] | ~ | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | <___> | <___> | NVI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| SF-SS | SUPPLY FAN START/STOP | ~ | ON/OFF | <___> | BO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | ~ | HVAC_COOL/ HVAC_HEAT/ HVAC_OFF | <___> | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | ~ | OPEN/CLOSED | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | MINIMUM OUTSIDE AIR FLOW SETTING | [____ CFM] | ~ | <___> |  | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE TEMPERATURE CONTROL: MA DAMPERS HEATING COIL COOLING COIL | OA-T | OUTSIDE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| MA-D-C | MIXED AIR DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT | [___] | ~ | <___> |  | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ X ] | X | <___> | <___> | ~ | ~ | ~
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT | [___] | ~ | <___> |  | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ X ] | X | <___> | <___> | ~ | ~ | ~
|  | MIXED AIR PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
| ZN-T | ZONE TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | [OCC ADJ] | [68-77 DEG F] | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ X ] | X | <___> | <___> | ~ | ~ | ~
| HTG-V-C | HEATING COIL VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| CLG-V-C | COOLING COIL VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | HEATING COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | COOLING COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | SA-T | SUPPLY AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | ALM/NORMAL | <___> | BI | ~ | [ ~ ] | [ ~ ] | ~ | <___> | <___> | ~ | ~ | ~ | ~ | [ALM] | [info] [crit] | [___]
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 7
SINGLE ZONE WITH DUAL TEMPERATURE COIL
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | ~ | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | SUPPLY FAN PROOF FAILED | [info] [crit] | [___]
| DT-DA-T-LL | DUAL TEMP COIL DISCHARGE AIR TEMP LOW LIMIT SWITCH | [39 DEG F] | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| SA-SMK | SUPPLY AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RA-SMK | RETURN AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | ~ | ~ | <___> | [___] | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [___] | <___> | <___> | ~ | ~ | ~
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | BLDG-T IS LESS THAN BLDG-T-LL | [info] [crit] | [___]
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT | [55 DEG F] | ~ | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | <___> | <___> | NVI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| SF-SS | SUPPLY FAN START/STOP | ~ | ON/OFF | <___> | BO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | ~ | HVAC_COOL/ HVAC_HEAT/ HVAC_OFF | <___> | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | ~ | OPEN/CLOSED | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | MINIMUM OUTSIDE AIR FLOW SETTING | [____ CFM] | ~ | <___> |  | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE TEMPERATURE CONTROL: MA DAMPERS HEATING COIL COOLING COIL | OA-T | OUTSIDE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| MA-D-C | MIXED AIR DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ X ] | X | <___> | <___> | ~ | ~ | ~
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ X ] | X | <___> | <___> | ~ | ~ | ~
|  | MIXED AIR PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
~
| DTWS-T | DUAL TEMP WATER SUPPLY TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| DTWS-T-SP | DUAL TEMP WATER SUPPLY TEMPERATURE SETPOINT | [___] | ~ | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-T | ZONE TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | [OCC ADJ] | [68-77 DEG F] | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | X | X | <___> | <___> | ~ | ~ | ~
| DT-V-C | DUAL TEMP COIL VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | DUAL TEMP COIL VALVE COOLING PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | DUAL TEMP COIL VALVE HEATING PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | SA-T | SUPPLY AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | ALM/NORMAL | <___> | BI | ~ | [ ~ ] | [ ~ ] | ~ | <___> | <___> | ~ | ~ | ~ | ~ | [ALM] | [info] [crit] | [___]
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 8
SINGLE ZONE WITH HEATING AND COOLING COILS AND RETURN AIR BYPASS
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | ~ | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | SUPPLY FAN PROOF FAILED | [info] [crit] | [___]
| HTG-DA-T-LL | HEATING COIL DISCHARGE AIR TEMP LOW LIMIT SWITCH | [39 DEG F] | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| SA-SMK | SUPPLY AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RA-SMK | RETURN AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | ~ | ~ | <___> | [___] | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [___] | <___> | <___> | ~ | ~ | ~
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | BLDG-T IS LESS THAN BLDG-T-LL | [info] [crit] | [___]
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT | [55 DEG F] | ~ | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | <___> | <___> | NVI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| SF-SS | SUPPLY FAN START/STOP | ~ | ON/OFF | <___> | BO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | ~ | HVAC_COOL/ HVAC_HEAT/ HVAC_OFF | <___> | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | ~ | OPEN/CLOSED | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | MINIMUM OUTSIDE AIR FLOW SETTING | [____ CFM] | ~ | <___> |  | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE TEMPERATURE CONTROL: MA DAMPERS HEATING COIL COOLING COIL BYPASS DAMPER | OA-T | OUTSIDE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| MA-D-C | MIXED AIR DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ X ] | X | <___> | <___> | ~ | ~ | ~
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ X ] | X | <___> | <___> | ~ | ~ | ~
|  | MIXED AIR PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
| ZN-T | ZONE TEMPERATURE | ~ | <___> | <___> | AI | ~ | X | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | [OCC ADJ] | [68-77 DEG F] | <___> | AI | ~ | X | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| HTG-V-C | HEATING COIL VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | X | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| CLG-V-C-2P | COOLING COIL VALVE COMMAND (2-POS) | ~ | OPEN/CLOSED | <___> | BO | [~] | X | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| BA-D-C | BYPASS AIR DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | X | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | BYPASS AIR DAMPER PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
|  | HEATING COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
OTHER POINTS | SA-T | SUPPLY AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | ALM/NORMAL | <___> | BI | ~ | [ ~ ] | [ ~ ] | ~ | <___> | <___> | ~ | ~ | ~ | ~ | [ALM] | [info] [crit] | [___]
| BA-FLT-P-HL | BYPASS AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | ALM/NORMAL | <___> | BI | ~ | [ ~ ] | [ ~ ] | ~ | <___> | <___> | ~ | ~ | ~ | ~ | [ALM] | [info] [crit] | [___]
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 9
SINGLE ZONE WITH HUMIDITY CONTROL
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | ~ | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | SUPPLY FAN PROOF FAILED | [info] [crit] | [___]
| PH-DA-T-LL | PREHEAT COIL DISCHARGE AIR TEMP LOW LIMIT SWITCH | [39 DEG F] | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| SA-SMK | SUPPLY AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RA-SMK | RETURN AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | ~ | ~ | <___> | [___] | ~ | ~ | ~ | ~ | ~ | ~ | [___] | [___] | <___> | <___> | ~ | ~ | ~
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | BLDG-T IS LESS THAN BLDG-T-LL | [info] [crit] | [___]
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT | [55 DEG F] | ~ | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | <___> | <___> | NVI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| SF-SS | SUPPLY FAN START/STOP | ~ | ON/OFF | <___> | BO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | ~ | HVAC_COOL/ HVAC_HEAT/ HVAC_OFF | <___> | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
OUTSIDE AIRFLOW | OA-D-2P | OUTSIDE AIR DAMPER COMMAND (2-POS) | ~ | OPEN/CLOSED | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | OUTSIDE AIR FLOW SETTING | [____ CFM] | ~ | <___> |  | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
PREHEAT COIL CONTROL | PH-DA-T | PREHEAT COIL DISCHARGE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | PH-DA-T IS MORE THAN 34 DEG F BELOW PH-DA-T-SP | [info] [crit]
| PH-DA-T-SP | PREHEAT COIL DISCHARGE AIR TEMPERATURE SETPOINT | ~ | <___> | <___> | AO | [~] | [ X ] | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| PH-V-C | PREHEAT COIL VALVE COMMAND | ~ | <0-100% OPEN> | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | PREHEAT COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE TEMPERATURE AND HUMIDITY CONTROL | ZN-T | ZONE TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | [OCC ADJ] | [68-77 DEG F] | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-RH | ZONE RELATIVE HUMIDITY | ~ | <0 - 100 % RH> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-RH IS MORE THAN 10% ABOVE OR BELOW ZN-RH-SP | [info] [crit] | [___]
| ZN-RH-SP | ZONE RELATIVE HUMIDITY SETPOINT | [___] | ~ | <___> | ~ | ~ | ~ | ~ | X | ~ | ~ | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| SA-RH | SUPPLY AIR RELATIVE HUMIDITY | ~ | <0 - 100 % RH> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | SA-RH IS ABOVE 90% RH | [info] [crit] | [___]
| SA-RH-SP | SUPPLY AIR RELATIVE HUMIDITY SETPOINT | 80% RH | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
| RH-V-C | REHEAT COIL VALVE COMMAND | ~ | <0-100% OPEN> | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| CLG-V-C | COOLING COIL VALVE COMMAND | ~ | <0-100% OPEN> | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| HUM-V-C | HUMIDIFIER VALVE COMMAND | ~ | <0-100% OPEN> | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | COOLING COIL VALVE PID LOOP SETTINGS FOR RH CONTROL | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | COOLING COIL VALVE PID LOOP SETTINGS FOR TEMP CONTROL | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | HEATING COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | HUMIDIFIER VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | SA-T | SUPPLY AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | [___] | ALM/NORMAL | <___> | BI | ~ | [ ~ ] | [ ~ ] | ~ | <___> | <___> | ~ | ~ | ~ | ~ | [ALM] | [info] [crit] | [___]
| OA-FLT-P-HL | OUTSIDE AIR FILTER PRESSURE HIGH LIMIT SWITCH | [___] | ALM/NORMAL | <___> | BI | ~ | [ ~ ] | [ ~ ] | ~ | <___> | <___> | ~ | ~ | ~ | ~ | [ALM] | [info] [crit] | [___]
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 10
DUAL DUCT WITH RETURN FAN
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | ~ | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | SUPPLY FAN PROOF FAILED | [info] [crit] | [___]
| RF-S | RETURN FAN STATUS | ~ | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | SUPPLY FAN PROOF FAILED | [info] [crit] | [___]
| MA-T-LL | MIXED AIR TEMPERATURE LOW LIMIT | [39 DEG F] | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| SA-SMK | SUPPLY AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RA-SMK | RETURN AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | ~ | ~ | <___> | [___] | ~ | ~ | ~ | ~ | ~ | ~ | [___] | [___] | <___> | <___> | ~ | ~ | ~
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | BLDG-T IS LESS THAN BLDG-T-LL | [info] [crit] | [___]
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT | [55 DEG F] | ~ | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | <___> | <___> | NVI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| SF-SS | SUPPLY FAN START/STOP | ~ | START/STOP | <___> | BO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | ~ | HVAC_COOL/ HVAC_HEAT/ HVAC_OFF | <___> | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | ~ | OPEN/CLOSED | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | MINIMUM OUTSIDE AIR FLOW SETTING | [____ CFM] | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
MIXED AIR TEMPERATURE CONTROL WITH ECONOMIZER | OA-T | OUTSIDE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| MA-D-C | MIXED AIR DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| MA-T | MIXED AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | X | <___> | <___> | ~ | ~ | ~
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | X | <___> | <___> | ~ | ~ | ~
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | MIXED AIR DAMPER PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
HOT DECK CONTROL | HD-T | HOT DECK TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| HD-T-SP | HOT DECK TEMPERATURE SETPOINT | [ RESET ] | ~ | <___> | ~ | ~ | [ X ] | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| HD-V-C | HOT DECK VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | HEATING COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
COLD DECK CONTROL | CD-T | COLD DECK TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| CD-T-SP | COLD DECK TEMPERATURE SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| CD-V-C | COLD DECK VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | COOLING COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE [1] TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | [OCC ADJ] | [68-77 DEG F] | <___> | AI | ~ | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-D-C | ZONE DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | ZONE DAMPER PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE [2] TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | [OCC ADJ] | [68-77 DEG F] | <___> | AI | ~ | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-D-C | ZONE DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | ZONE DAMPER PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | RA-T | RETURN AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | ALM/NORMAL | <___> | BI | ~ | [ ~ ] | [ ~ ] | ~ | <___> | <___> | ~ | ~ | ~ | ~ | [ALM] | [info] [crit] | [___]
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 11
MULTIZONE WITH RETURN FAN
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | ~ | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | SUPPLY FAN PROOF FAILED | [info] [crit] | [___]
| RF-S | RETURN FAN STATUS | ~ | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | SUPPLY FAN PROOF FAILED | [info] [crit] | [___]
| MA-T-LL | MIXED AIR TEMPERATURE LOW LIMIT | [39 DEG F] | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| SA-SMK | SUPPLY AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RA-SMK | RETURN AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | ~ | ~ | <___> | [___] | ~ | ~ | ~ | ~ | ~ | ~ | [___] | [___] | <___> | <___> | ~ | ~ | ~
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | BLDG-T IS LESS THAN BLDG-T-LL | [info] [crit] | [___]
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT | [55 DEG F] | ~ | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | <___> | <___> | NVI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| SF-SS | SUPPLY FAN START/STOP | ~ | START/STOP | <___> | BO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | ~ | HVAC_COOL/ HVAC_HEAT/ HVAC_OFF | <___> | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | ~ | OPEN/CLOSED | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | MINIMUM OUTSIDE AIR FLOW SETTING | [____ CFM] | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
MIXED AIR TEMPERATURE CONTROL WITH ECONOMIZER | OA-T | OUTSIDE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| MA-D-C | MIXED AIR DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| MA-T | MIXED AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | X | <___> | <___> | ~ | ~ | ~
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | X | <___> | <___> | ~ | ~ | ~
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | MIXED AIR DAMPER PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
HOT DECK CONTROL | HD-T | HOT DECK TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| HD-T-SP | HOT DECK TEMPERATURE SETPOINT | [ RESET ] | ~ | <___> | ~ | ~ | [ X ] | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| HD-V-C | HOT DECK VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | HEATING COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
COLD DECK CONTROL | CD-T | COLD DECK TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| CD-T-SP | COLD DECK TEMPERATURE SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| CD-V-C | COLD DECK VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | COOLING COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE [1] TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | [OCC ADJ] | [68-77 DEG F] | <___> | AI | ~ | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-D-C | ZONE DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | ZONE DAMPER PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE [2] TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | [OCC ADJ] | [68-77 DEG F] | <___> | AI | ~ | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-D-C | ZONE DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | ZONE DAMPER PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | RA-T | RETURN AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | ALM/NORMAL | <___> | BI | ~ | [ ~ ] | [ ~ ] | ~ | <___> | <___> | ~ | ~ | ~ | ~ | [ALM] | [info] [crit] | [___]
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 12
MULTIZONE WITH HOT DECK BYPASS WITH RETURN FAN
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | ~ | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | SUPPLY FAN PROOF FAILED | [info] [crit] | [___]
| RF-S | RETURN FAN STATUS | ~ | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | SUPPLY FAN PROOF FAILED | [info] [crit] | [___]
| MA-T-LL | MIXED AIR TEMPERATURE LOW LIMIT | [39 DEG F] | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| SA-SMK | SUPPLY AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RA-SMK | RETURN AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | ~ | ~ | <___> | [___] | ~ | ~ | ~ | ~ | ~ | ~ | [___] | [___] | <___> | <___> | ~ | ~ | ~
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | BLDG-T IS LESS THAN BLDG-T-LL | [info] [crit] | [___]
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT | [55 DEG F] | ~ | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | <___> | <___> | NVI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| SF-SS | SUPPLY FAN START/STOP | ~ | START/STOP | <___> | BO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | ~ | HVAC_COOL/ HVAC_HEAT/ HVAC_OFF | <___> | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
MINIMUM OUTSIDE AIRFLOW | MINOA-D-2P | MINIMUM OUTSIDE AIR DAMPER COMMAND (2-POS) | ~ | OPEN/CLOSED | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | MINIMUM OUTSIDE AIR FLOW SETTING | [____ CFM] | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
MIXED AIR TEMPERATURE CONTROL WITH ECONOMIZER | OA-T | OUTSIDE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| OA-D-C | OUTSIDE AIR DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| MA-T | MIXED AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | X | <___> | <___> | ~ | ~ | ~
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | X | <___> | <___> | ~ | ~ | ~
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | MIXED AIR DAMPER PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
COLD DECK CONTROL | CLG-DA-T | COOLING COIL DISCHARGE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| CLG-DA-T-SP | COOLING COIL DISCHARGE AIR TEMPERATURE SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| CD-V-C | COLD DECK VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | ~ | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | COOLING COIL VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE [1] TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | [OCC ADJ] | [68-77 DEG F] | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-D-C | ZONE DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | ZONE DAMPER PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
| ZN-V-C | ZONE HEATING VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | ZONE HEATING VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE [2] TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T IS MORE THAN 37 DEG F ABOVE OR BELOW ZN-T-SP | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | [OCC ADJ] | [68-77 DEG F] | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-D-C | ZONE DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | ZONE DAMPER PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
| ZN-V-C | ZONE HEATING VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | ZONE HEATING VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | RA-T | RETURN AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | ALM/NORMAL | <___> | BI | ~ | [ ~ ] | [ ~ ] | ~ | <___> | <___> | ~ | ~ | ~ | ~ | [ALM] | [info] [crit] | [___]
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 13
VAV [WITH][WITHOUT] RETURN FAN
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | SF-S | SUPPLY FAN STATUS | ~ | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | SUPPLY FAN PROOF FAILED | [info] [crit] | [___]
| RF-S | RETURN FAN STATUS | ~ | ON/OFF | <___> | BI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | RETURN FAN PROOF FAILED | [info] [crit] | [___]
| SA-SMK | SUPPLY AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RA-SMK | RETURN AIR SMOKE | ~ | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| CLG-DA-T-LL | COOLING COIL DISCHARGE AIR TEMP LOW LIMIT | 39 DEG F | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| SA-P-HL | SUPPLY AIR PRESSURE HIGH LIMIT | [___ IWC] | ALM/NORMAL | <___> | BI | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| RST-BUT | SYSTEM RESET BUTTON (FOR SAFETIES) | ~ | ~ | <___> | [___] | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [___]
START/STOP | BLDG-T | BUILDING TEMPERATURE (NIGHT STAT) | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | BLDG-T LESS THAN BLDG-T-LL | [info] [crit] | [___]
| BLDG-T-LL | BUILDING TEMPERATURE LOW LIMIT SETPOINT | [55 DEG F] | ~ | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) |  | <___> | <___> | NVI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| SF-SS | SUPPLY FAN START/STOP | ~ | ON/OFF | <___> | BO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| RF-SS | RETURN FAN START/STOP | ~ | ON/OFF | <___> | BO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (HTG AND/OR CLG REQUEST) (SEE NOTE) | ~ | HVAC_COOL/ [HVAC_HEAT] | <___> | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
SUPPLY FAN CAPACITY CONTROL | SA-P | SUPPLY AIR PRESSURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | *SA-P MORE THAN 20% ABOVE OR BELOW SA-P-SP | [info] [crit] | <___>
| SA-P-SP | SUPPLY AIR PRESSURE SETPOINT | <___> | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| SF-C | SUPPLY FAN COMMAND | ~ | 0-100% | <___> | AO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | SUPPLY FAN PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
RETURN FAN CAPACITY CONTROL | SA-F | SUPPLY AIR FLOW | ~ | [0 - ___ CFM] | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| RA-F | RETURN AIR FLOW | ~ | [0 - ___ CFM] | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| F-DIFF-SP | FLOW DIFFERENCE SETPOINT | [___ CFM] | ~ | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| RF-C | RETURN FAN COMMAND | ~ | 0-100% | <___> | AO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | RETURN FAN PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
MINIMUM OUTSIDE AIR | MINOA-F | MINIMUM OUTSIDE AIR FLOW | ~ | [0 - ___ CFM] | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | MINOA-F LESS THAN 80% OF MINOA-F-SP | [info] [crit] | [___]
| MINOA-F-SP | MINIMUM OUTSIDE AIR FLOW SETPOINT (SETTING) | [___ CFM] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| MINOA-D-C | MINIMUM OUTSIDE AIR DAMPER COMMAND | ~ | <0-100% OPEN> | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | MINIMUM OUTSIDE AIR DAMPER PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | ~ | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
MIXED AIR TEMPERATURE CONTROL WITH ECONOMIZER | OA-T | OUTSIDE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| MA-D-C | MIXED AIR DAMPER COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| MA-T | MIXED AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| MA-T-SP | MIXED AIR TEMPERATURE SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ECO-HL-SP | ECONOMIZER HIGH LIMIT SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ECO-LL-SP | ECONOMIZER LOW LIMIT SETPOINT | [___] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | MIXED AIR DAMPER PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
SUPPLY AIR TEMPERATURE | SA-T | SUPPLY AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | *SA-T MORE THAN 10 DEG F ABOVE OR BELOW SETPOINT | [info] [crit] | [___]
| SA-T-SP | SUPPLY AIR TEMPERATURE SETPOINT | [55 DEG F] | ~ | <___> | ~ | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| CLG-V-C | COOLING VALVE COMMAND | ~ | <0-100% OPEN> | <___> | AO | [~] | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | COOLING VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
OTHER POINTS | RA-T | RETURN AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| MA-FLT-P-HL | MIXED AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | ALM/NORMAL | <___> | BI | ~ | [ ~ ] | ~ | ~ | <___> | <___> | ~ | ~ | ~ | ~ | TRUE | [info] [crit] | [___]
| OA-FLT-P-LL | OUTSIDE AIR FILTER PRESSURE HIGH LIMIT SWITCH | <___> | ALM/NORMAL | <___> | BI | ~ | [ ~ ] | ~ | ~ | <___> | <___> | ~ | ~ | ~ | ~ | TRUE | [info] [crit] | [___]
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
COOLING ONLY VAV BOX
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | <___> | <UNIT MANUFACTURER'S PROOF> (SEE NOTES) | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [___]
| <___> | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES> | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
START/STOP | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | ~ | < ~ > | NVI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | ~ | ~ | < ~ > | BI | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| EFF-OCC | EFFECTIVE OCCUPANCY | ~ | OCC/UNOCC | < ~ > | NVO | ~ | [ ~ ] | X | [ ~ ] | <___> | OCCUPANCY | ~ | ~ | ~ | ~ | ~ | ~ | ~
< ~ >
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE ** | ~ | <___> | < ~ > | AI | ~ | [ ~ ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T MORE THAN 77 DEG F OR BELOW 68 DEG F | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | OCCUPANT ADJUSTABLE | [ 68-77 DEG F ] | < ~ > | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| VAV-SA-F | VAV SUPPLY AIR FLOW | ~ | <___> | < ~ > | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| VAV-SA-F-SP | VAV SUPPLY AIR FLOW SETPOINT | RESET SCHED | ~ | < ~ > | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| VAV-D-C | VAV DAMPER COMMAND | ~ | <0-100% OPEN> | < ~ > | AO | ~ | [ ~ ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | VAV DAMPER PID LOOP SETTINGS | <___> | ~ | < ~ > | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH A DOUBLE ASTERISK (**) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN 30 MINUTES.
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
VAV BOX WITH REHEAT
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | <___> | <UNIT MANUFACTURER'S PROOF> (SEE NOTES) | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [___]
| <___> | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES> | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
START/STOP | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | ~ | < ~ > | NVI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | ~ | ~ | < ~ > | BI | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| EFF-OCC | EFFECTIVE OCCUPANCY | ~ | OCC/UNOCC | < ~ > | NVO | ~ | [ ~ ] | X | [ ~ ] | <___> | OCCUPANCY | [ ~ ] | ~ | ~ | ~ | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (SEE NOTES) | ~ | HVAC_HEAT/ HVAC_OFF | < ~ > | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE ** | ~ | <___> | < ~ > | AI | ~ | [ ~ ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T MORE THAN 77 DEG F OR BELOW 68 DEG F | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | OCCUPANT ADJUSTABLE | [68-77 DEG F] | < ~ > | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-T-SP-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE | [ 82 DEG F ] | ~ | < ~ > | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| VAV-SA-F | VAV SUPPLY AIR FLOW | ~ | <___> | < ~ > | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| VAV-SA-F-SP | VAV SUPPLY AIR FLOW SETPOINT | RESET SCHED | ~ | < ~ > | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | ~ | ~ | ~ | ~ | ~ | ~
| VAV-D-C | VAV DAMPER COMMAND | ~ | <0-100% OPEN> | < ~ > | AO | ~ | [ ~ ] | X | X | <___> | <___> | [ ~ ] | ~ | ~ | ~ | ~ | ~ | ~
| VAV-V-C | VAV <REHEAT VALVE> <HEAT ELEMENT> COMMAND | ~ | <0-100% OPEN> | < ~ > | <AO> | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | ~ | ~ | ~ | ~ | ~ | ~
|  | ZONE TEMPERATURE SETPOINT DEADBAND | [36 DEG F] | ~ | < ~ > | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | VAV DAMPER PID LOOP SETTINGS | <___> | ~ | < ~ > | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | VAV VALVE PID LOOP SETTINGS | <___> | ~ | < ~ > | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | VAV-DA-T | VAV DISCHARGE AIR TEMPERATURE | ~ | <___> | < ~ > | AI | ~ | [ ~ ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH A DOUBLE ASTERISK (**) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN 30 MINUTES.
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
SERIES FAN POWERED VAV BOX [WITH REHEAT]
AND
PARALLEL FAN POWERED VAV BOX [WITH REHEAT]
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | <___> | <UNIT MANUFACTURER'S PROOF> (SEE NOTES) | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [___]
| <___> | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES> | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
START/STOP | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | ~ | < ~ > | NVI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | ~ | ~ | < ~ > | BI | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| EFF-OCC | EFFECTIVE OCCUPANCY | ~ | OCC/UNOCC | < ~ > | NVO | ~ | [ ~ ] | X | [ ~ ] | <___> | OCCUPANCY | [ ~ ] | ~ | ~ | ~ | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (SEE NOTES) | ~ | HVAC_HEAT/ HVAC_OFF | < ~ > | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE ** | ~ | <___> | < ~ > | AI | ~ | [ ~ ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T MORE THAN 77 DEG F OR BELOW 68 DEG F | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | OCCUPANT ADJUSTABLE | [68-77 DEG F] | < ~ > | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-T-SP-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE | [ 82 DEG F ] | ~ | < ~ > | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| VAV-SA-F | VAV SUPPLY AIR FLOW | ~ | <___> | < ~ > | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
| VAV-SA-F-SP | VAV SUPPLY AIR FLOW SETPOINT | RESET SCHED | ~ | < ~ > | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | ~ | ~ | ~ | ~ | ~ | ~
| VAV-D-C | VAV DAMPER COMMAND | ~ | <0-100% OPEN> | < ~ > | AO | ~ | [ ~ ] | X | X | <___> | <___> | [ ~ ] | ~ | ~ | ~ | ~ | ~ | ~
| VAV-V-C | VAV <REHEAT VALVE> <HEAT ELEMENT> COMMAND | ~ | <0-100% OPEN> | < ~ > | <AO> | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | ~ | ~ | ~ | ~ | ~ | ~
| VAV-FAN-SS | VAV FAN START/STOP | ~ | START/STOP | < ~ > | BO | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | ~ | ~ | ~ | ~ | ~ | ~
|  | ZONE TEMPERATURE SETPOINT DEADBAND | <36 DEG F> | ~ | < ~ > | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | VAV DAMPER PID LOOP SETTINGS | <___> | ~ | < ~ > | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | VAV VALVE PID LOOP SETTINGS | <___> | ~ | < ~ > | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | VAV-DA-T | VAV DISCHARGE AIR TEMPERATURE | ~ | <___> | < ~ > | AI | ~ | [ ~ ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [___]
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH A DOUBLE ASTERISK (**) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN 30 MINUTES.
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 14
UNIT HEATER AND CABINET UNIT HEATER
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | <___> | <UNIT MANUFACTURER'S PROOF> (SEE NOTES) | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [___]
| <___> | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES> | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
START/STOP | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | OCC/UNOCC | < ~ > | NVI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | ~ | OCC/UNOCC | < ~ > | BI | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| EFF-OCC | EFFECTIVE OCCUPANCY | ~ | OCC/UNOCC | < ~ > | NVO | ~ | [ ~ ] | X | [ ~ ] | <___> | OCCUPANCY | ~ | ~ | ~ | ~ | ~ | ~ | ~
| OFF / AUTO | UNIT OFF / AUTO SWITCH | ~ | ~ | < ~ > | BI | ~ | ~ | [ ~ ] | [ ~ ] | <___> | <___> | ~ | [ ~ ] | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (SEE NOTES) | ~ | HVAC_HEAT/ HVAC_OFF | < ~ > | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE ** | ~ | <___> | < ~ > | AI | ~ | [ ~ ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T MORE THAN 77 DEG F OR BELOW 68 DEG F | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | OCCUPANT ADJUSTABLE | [68-77 DEG F] | < ~ > | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-T-SP-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE | [ 82 DEG F ] | ~ | < ~ > | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| HTG-V-C | HEATING VALVE COMMAND | ~ | 0-100% OPEN | < ~ > | AO | ~ | [ ~ ] | X | X | <___> | <___> | ~ | X | ~ | ~ | ~ | ~ | ~
| SF-SS | SUPPLY FAN START/STOP | ~ | [OFF/LO/MED/HI] | < ~ > | BO | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | HEATING VALVE PID LOOP SETTINGS | <___> | ~ | < ~ > | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH A DOUBLE ASTERISK (**) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN 30 MINUTES.
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
GAS-FIRED INFRARED HEATER
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | <___> | <UNIT MANUFACTURER'S PROOF> (SEE NOTES) | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [___]
| <___> | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES> | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | ~ | OCC/UNOCC | < ~ > | BI | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| EFF-OCC | EFFECTIVE OCCUPANCY | ~ | OCC/UNOCC | < ~ > | NVO | ~ | [ ~ ] | X | [ ~ ] | <___> | OCCUPANCY | ~ | ~ | ~ | ~ | ~ | ~ | ~
| ON / OFF / AUTO | UNIT OFF / AUTO SWITCH | ~ | ~ | < ~ > | BI | ~ | ~ | [ ~ ] | [ ~ ] | <___> | <___> | ~ | [ ~ ] | <___> | <___> | ~ | ~ | ~
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE ** | ~ | <___> | < ~ > | AI | ~ | [ ~ ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T MORE THAN 77 DEG F OR BELOW 68 DEG F | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | OCCUPANT ADJUSTABLE | [68-77 DEG F] | < ~ > | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-T-SP-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE | [ 82 DEG F ] | ~ | < ~ > | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| HTG-IR-2P | INFRARED HEATER ON/OFF COMMAND | ~ | ON/OFF | < ~ > | BO | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH A DOUBLE ASTERISK (**) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN 30 MINUTES.
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
PERIMETER RADIATION
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | <___> | <UNIT MANUFACTURER'S PROOF> (SEE NOTES) | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [___]
| <___> | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES> | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
START/STOP | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | OCC/UNOCC | < ~ > | NVI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | ~ | OCC/UNOCC | < ~ > | BI | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| EFF-OCC | EFFECTIVE OCCUPANCY | ~ | OCC/UNOCC | < ~ > | NVO | ~ | [ ~ ] | X | [ ~ ] | <___> | OCCUPANCY | [ ~ ] | ~ | ~ | ~ | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (SEE NOTES) | ~ | HVAC_HEAT/ HVAC_OFF | < ~ > | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE TEMPERATURE CONTROL | ZN-T | ZONE TEMPERATURE ** | ~ | <___> | < ~ > | AI | ~ | [ ~ ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T MORE THAN 77 DEG F OR BELOW 68 DEG F | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | OCCUPANT ADJUSTABLE | [68-77 DEG F] | < ~ > | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-T-SP-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE | [ 82 DEG F ] | ~ | < ~ > | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| HTG-V-C | HEATING VALVE COMMAND | ~ | <0-100% OPEN> | < ~ > | AO | ~ | [ ~ ] | X | X | <___> | <___> | [ ~ ] | ~ | ~ | ~ | ~ | ~ | ~
|  | HEATING VALVE PID LOOP SETTINGS | <___> | ~ | < ~ > | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH A DOUBLE ASTERISK (**) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN 30 MINUTES.
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.
DUAL TEMPERATURE FAN COIL UNIT
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | <___> | <UNIT MANUFACTURER'S PROOF> (SEE NOTES) | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | [___]
| <___> | <UNIT MANUFACTURER'S SAFETIES> (SEE NOTES> | <___> | ALM/NORMAL | < ~ > | <BI> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ALM | [info] [crit] | [___]
START/STOP | SYS-OCC | OCCUPANCY INPUT (FROM SYSTEM SCHEDULER) | ~ | OCC/UNOCC | < ~ > | NVI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | SEE NOTES |  |  |  | ~ | ~ | ~
| ZN-OCC | ZONE OCCUPANCY INPUT (OCCUPANCY SENSOR) | ~ | OCC/UNOCC | < ~ > | BI | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| EFF-OCC | EFFECTIVE OCCUPANCY | ~ | OCC/UNOCC | < ~ > | NVO | ~ | [ ~ ] | X | [ ~ ] | <___> | OCCUPANCY | [ ~ ] | ~ | ~ | ~ | ~ | ~ | ~
| UNIT STATUS | UNIT STATUS (SEE NOTES) | ~ | HVAC_HEAT/ HVAC_OFF | < ~ > | NVO | ~ | [ ~ ] | [ X ] | [ ~ ] | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
ZONE TEMPERATURE CONTROL | DTWS-T | DUAL TEMP WATER SUPPLY TEMPERATURE | ~ | <___> | < ~ > | <AI> | ~ | [ ~ ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| DTWS-T-SP | DUAL TEMP WATER SUPPLY TEMPERATURE SETPOINT | ~ | <___> | < ~ > | <AI> | ~ | [ ~ ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| ZN-T | ZONE TEMPERATURE ** | ~ | <___> | < ~ > | AI | ~ | [ ~ ] | X | X | <___> | TEMP_P | ~ | ~ | ~ | ~ | ** ZN-T MORE THAN 77 DEG F OR BELOW 68 DEG F | [info] [crit] | [___]
| ZN-T-SP | ZONE TEMPERATURE SETPOINT | OCCUPANT ADJUSTABLE | [68-77 DEG F] | < ~ > | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| ZN-T-SP-HTG-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE | [ 60 DEG F ] | ~ | < ~ > | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| ZN-T-SP-CLG-UNOCC | ZONE TEMPERATURE SETPOINT FOR UNOCCUPIED MODE | [ 82 DEG F ] | ~ | < ~ > | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| DT-V-C | DUAL TEMP VALVE COMMAND | ~ | <0-100% OPEN> | < ~ > | AO | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| OFF/AUTO | UNIT OFF/AUTO SWITCH | ~ | OFF/AUTO | < ~ > | BI | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | ~ | ~ | ~ | ~ | ~
| SF-SS | SUPPLY FAN START/STOP | ~ | [OFF/LO/MED/HI] | < ~ > | BO | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
|  | DUAL TEMP VALVE PID LOOP SETTINGS | ~ | ~ | < ~ > | ~ | ~ | [ ~ ] | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 15
HYDRONIC HEATING HOT WATER FROM DISTRIBUTED STEAM CONVERTER
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | HW-PMP-S | HOT WATER PUMP STATUS | ~ | ON/OFF | <___> |  | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | [___]
<___>
START/STOP | SYS-ENA | SYSTEM ENABLE | ~ | ENABLE/DISABLE | <___> | <NVI> | ~ | [ X ] | [ X ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| HW-PMP-SS | HOT WATER PUMP START/STOP | ~ | START/STOP | <___> | BO | [~] | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | HEATING MODE UNIT STATUS (SEE NOTES) | ~ | ON/OFF | <___> | NVO | ~ | ~ | [ X ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | [ ~ ]
HEAT EXCHANGER VALVE CONTROL (STEAM) | OA-T | OUTSIDE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| HWS-T | HOT WATER SUPPLY TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | HWS-T MORE THAN 41 DEG F ABOVE OR BELOW HWS-T-SP | [info] [crit] | [___]
| HWS-T-SP | HOT WATER SUPPLY TEMPERATURE SETPOINT | [RESET] | ~ | <___> | ~ | ~ | [ X ] | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| STM-V-C | STEAM VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | [ ~ ]
|  | STEAM VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
SYSTEMS SERVED | HTG-RQST1 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | ~ | HVAC_HEAT/ HVAC_OFF | <___> | NVI | ~ | ~ | X | ~ | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
| HTG-RQST2 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | ~ | HVAC_HEAT/ HVAC_OFF | <___> | NVI | ~ | ~ | X | ~ | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | HWR-T | HOT WATER RETURN TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | ~
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 16
HYDRONIC HEATING HOT WATER FROM DISTRIBUTED HTHW CONVERTER
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | HW-PMP-S | HOT WATER PUMP STATUS | ~ | ON/OFF | <___> |  | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | [___]
<___>
START/STOP | SYS-ENA | SYSTEM ENABLE | ~ | ENABLE/DISABLE | <___> | <NVI> | ~ | [ X ] | [ X ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| HW-PMP-SS | HOT WATER PUMP START/STOP | ~ | START/STOP | <___> | BO | [~] | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | HEATING MODE UNIT STATUS (SEE NOTES) | ~ | ON/OFF | <___> | NVO | ~ | ~ | [ X ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | [ ~ ]
HEAT EXCHANGER VALVE CONTROL (STEAM) | OA-T | OUTSIDE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| HWS-T | HOT WATER SUPPLY TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | HWS-T MORE THAN 41 DEG F ABOVE OR BELOW HWS-T-SP | [info] [crit] | [___]
| HWS-T-SP | HOT WATER SUPPLY TEMPERATURE SETPOINT | [RESET] | ~ | <___> | ~ | ~ | [ X ] | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| HTHW-V-C | HTHW VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | [ ~ ]
|  | HTHW VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
SYSTEMS SERVED | HTG-RQST1 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | ~ | HVAC_HEAT/ HVAC_OFF | <___> | NVI | ~ | ~ | X | ~ | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
| HTG-RQST2 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | ~ | HVAC_HEAT/ HVAC_OFF | <___> | NVI | ~ | ~ | X | ~ | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | HWR-T | HOT WATER RETURN TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | ~
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 17
HYDRONIC HEATING HOT WATER FROM SINGLE BUILDING BOILER
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | HW-PMP-S | HOT WATER PUMP STATUS | ~ | ON/OFF | <___> |  | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | [___]
<___>
START/STOP | SYS-ENA | SYSTEM ENABLE | ~ | ENABLE/DISABLE | <___> | <NVI> | ~ | [ X ] | [ X ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| HW-PMP-SS | HOT WATER PUMP START/STOP | ~ | START/STOP | <___> | BO | [~] | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | HEATING MODE UNIT STATUS (SEE NOTES) | ~ | ON/OFF | <___> | NVO | ~ | ~ | [ X ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | [ ~ ]
HOT WATER TEMPERATURE CONTROL | OA-T | OUTSIDE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| HWS-T | HOT WATER SUPPLY TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | HWS-T MORE THAN 41 DEG F ABOVE OR BELOW HWS-T-SP | [info] [crit] | [___]
| HWS-T-SP | HOT WATER SUPPLY TEMPERATURE SETPOINT | [RESET] | ~ | <___> | ~ | ~ | [ X ] | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| HW-V-C | HOT WATER VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | [ ~ ]
|  | HOT WATER VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
SYSTEMS SERVED | HTG-RQST1 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | ~ | HVAC_HEAT/ HVAC_OFF | <___> | NVI | ~ | ~ | X | ~ | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
| HTG-RQST2 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | ~ | HVAC_HEAT/ HVAC_OFF | <___> | NVI | ~ | ~ | X | ~ | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | HWR-T | HOT WATER RETURN TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | ~
| BLR-S | BOILER STATUS (STATE) | ~ | START/STOP | <___> | <BI> | ~ | [ X ] | X | [ X ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 18
HYDRONIC DUAL-TEMPERATURE SYSTEM WITH STEAM HEAT EXCHANGER AND CHILLED WATER
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | HX-P-LL | HEAT EXCHANGER DIFFERENTIAL PRESSURE LOW LIMIT | ~ | FLOW/NO FLOW | <___> | BI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | * HWS FLOW PROOF FAILED | [info] [crit] | [___]
| DT-PMP-S | DUAL TEMP PUMP STATUS | ~ | ON/OFF | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | [___]
START/STOP | SYS-ENA | SYSTEM ENABLE | ~ | ENABLE/DISABLE | <___> | <NVI> | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| HTG/COOL-MOD | HEATING/COOLING MODE SWITCH | ~ | HEAT/COOL | <___> | BI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| DT-PMP-SS | DUAL TEMP PUMP START/STOP COMMAND | ~ | START/STOP | <___> | BO | [~] | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | HEATING MODE UNIT STATUS (SEE NOTES) | ~ | ON/OFF | <___> | NVO | ~ | ~ | [ X ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | [ ~ ]
DUAL TEMP SWITCHOVER | DTWR-T | DUAL-TEMP WATER RETURN TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| DTWR-T-LL | DUAL-TEMP WATER RETURN TEMPERATURE LOW LIMIT | 65 DEG F | ~ | <___> | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| DTWR-T-HL | DUAL-TEMP WATER RETURN TEMPERATURE HIGH LIMIT | 85 DEG F | ~ | <___> | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| DT-V-2P | DUAL-TEMP SWITCHOVER VALVE | ~ | HEAT/COOL | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| CHLR-ENA | CHILLER ENABLE | ~ | ENABLE/DISABLE | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
HEAT EXCHANGER VALVE CONTROL (STEAM) | OA-T | OUTSIDE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| HWS-T | HOT WATER SUPPLY TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | DTWS-T MORE THAN 41 DEG F ABOVE OR BELOW DTWS-T-SP | [info] [crit] | [___]
| HWS-T-SP | HOT WATER SUPPLY TEMPERATURE SETPOINT | [RESET] | ~ | <___> | ~ | ~ | [ X ] | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| STM-V-C | STEAM VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | [ ~ ]
|  | STEAM VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
SYSTEMS SERVED | HTG-RQST1 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | ~ | HVAC_HEAT/ HVAC_OFF | <___> | NVI | ~ | ~ | X | ~ | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
| HTG-RQST2 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | ~ | HVAC_HEAT/ HVAC_OFF | <___> | NVI | ~ | ~ | X | ~ | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | HWR-T | HOT WATER RETURN TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | ~
| DTWS-T | DUAL-TEMP WATER SUPPLY TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | ~
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 19
HYDRONIC DUAL-TEMPERATURE SYSTEM WITH HIGH TEMPERATURE HOT WATER HEAT EXCHANGER AND CHILLED WATER
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
PROOFS & SAFETIES | HX-P-LL | HEAT EXCHANGER DIFFERENTIAL PRESSURE LOW LIMIT | ~ | FLOW/NO FLOW | <___> | BI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | * HWS FLOW PROOF FAILED | [info] [crit] | [___]
| DT-PMP-S | DUAL TEMP PUMP STATUS | ~ | ON/OFF | <___> | ~ | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | [___]
START/STOP | SYS-ENA | SYSTEM ENABLE | ~ | ENABLE/DISABLE | <___> | <NVI> | ~ | [ X ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| HTG/COOL-MOD | HEATING/COOLING MODE SWITCH | ~ | HEAT/COOL | <___> | BI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| DT-PMP-SS | DUAL TEMP PUMP START/STOP COMMAND | ~ | START/STOP | <___> | BO | [~] | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| UNIT STATUS | HEATING MODE UNIT STATUS (SEE NOTES) | ~ | ON/OFF | <___> | NVO | ~ | ~ | [ X ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | [ ~ ]
DUAL TEMP SWITCHOVER | DTWR-T | DUAL-TEMP WATER RETURN TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | [ ~ ]
| DTWR-T-LL | DUAL-TEMP WATER RETURN TEMPERATURE LOW LIMIT | 65 DEG F | ~ | <___> | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| DTWR-T-HL | DUAL-TEMP WATER RETURN TEMPERATURE HIGH LIMIT | 85 DEG F | ~ | <___> | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| DT-V-2P | DUAL-TEMP SWITCHOVER VALVE | ~ | HEAT/COOL | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| CHLR-ENA | CHILLER ENABLE | ~ | ENABLE/DISABLE | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
HEAT EXCHANGER VALVE CONTROL (HTHW) | OA-T | OUTSIDE AIR TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
| HWS-T | HOT WATER SUPPLY TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | X | <___> | <___> | ~ | ~ | ~ | ~ | DTWS-T MORE THAN 41 DEG F ABOVE OR BELOW DTWS-T-SP | [info] [crit] | [___]
| HWS-T-SP | HOT WATER SUPPLY TEMPERATURE SETPOINT | [RESET] | ~ | <___> | ~ | ~ | [ X ] | X | X | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
| HTHW-V-C | HTHW VALVE COMMAND | ~ | 0-100% OPEN | <___> | AO | [~] | [ X ] | X | [ X ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | [ ~ ]
|  | HTHW VALVE PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
SYSTEMS SERVED | HTG-RQST1 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | ~ | HVAC_HEAT/ HVAC_OFF | <___> | NVI | ~ | ~ | X | ~ | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
| HTG-RQST2 | HTG RQST FROM: AHU [ ___ ], BUILDING [ ___ ] | ~ | HVAC_HEAT/ HVAC_OFF | <___> | NVI | ~ | ~ | X | ~ | <___> | HVAC_STATUS | ~ | ~ | ~ | ~ | ~ | ~ | ~
OTHER POINTS | HWR-T | HOT WATER RETURN TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | ~
| DTWS-T | DUAL-TEMP WATER SUPPLY TEMPERATURE | ~ | <___> | <___> | AI | ~ | [ X ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | [ ~ ] | ~ | ~
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 20
HYDRONIC SECONDARY WITH CONSTANT SPEED PUMPING
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
START/STOP | SYS-ENA | SYSTEM ENABLE | ~ | ~ | <___> | <NVI> | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| SEC-PMP-SS | CHILLED WATER PUMP START/STOP | ~ | START/STOP | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| SEC-PMP-S | CHILLED WATER PUMP STATUS | ~ | ON/OFF | <___> | BI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.

## 21
SECONDARY HYDRONIC WITH VARIABLE SPEED PUMPING
NODE: <DDC##>
NODE LOCATION: <___>
NODE ADDRESS: Domain = <___>, Subnet = <___>, Node = <___> | [7 empty] | LDP AND M&C DISPLAY |  |  |  |  | OVERRIDES |  |  |  | ALARMS
NODE ID: <___> | [7 empty] | LDP VIEW REQ'D | M&C |  | SNVT NAME | SNVT TYPE | LDP OVRD REQ'D | M&C OVRD REQ'D |  |  | ALARM CONDITION (SEE NOTES) | ALARM PRIORITY | M&C ROUTING
FUNCTION | NAME | DESCRIPTION | SETTING (WITH UNITS) | RANGE (WITH UNITS) | nci/CPT NAME | IO TYPE | HOA REQ'D |  | DISP REQ'D | TREND REQ'D |  |  |  |  | SNVT NAME | SNVT TYPE
START/STOP | SYS-ENA | SYSTEM ENABLE | ~ | ~ | <___> | <NVI> | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| SEC-PMP-SS | CHILLED WATER PUMP START/STOP | ~ | START/STOP | <___> | BO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~
| SEC-PMP-S | CHILLED WATER PUMP STATUS | ~ | ON/OFF | <___> | BI | ~ | [ ~ ] | X | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~
~
PRESSURE CONTROL | SEC-PMP-C | CHILLED WATER VFD PUMP SPEED COMMAND | ~ | <0-100%> | <___> | AO | [~] | [ ~ ] | X | [ ~ ] | <___> | <___> | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | ~ | [ ~ ]
| SEC-P | CHILLED WATER SUPPLY PRESSURE | ~ | <___> | <___> | AI | ~ | ~ | [ ~ ] | [ ~ ] | <___> | <___> | ~ | ~ | ~ | ~ | * CWS-P MORE THAN 25% ABOVE OR BELOW CWS-P-SP | [info] [crit] | [___]
| SEC-P-SP | CHILLED WATER SUPPLY PRESSURE SETPOINT | [___] | ~ | <___> | ~ | ~ | [ ~ ] | [ ~ ] | [ ~ ] | <___> | <___> | [ ~ ] | X | <___> | <___> | ~ | ~ | ~
|  | CHILLED WATER PUMP PID LOOP SETTINGS | <___> | ~ | <___> | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~ | ~
Notes:
1) | THE CONTRACTOR SHALL COMPLETE THE POINTS SCHEDULE AS SPECIFIED AND AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS DRAWING.
2) | UNIT MANUFACTURERS PROOFS AND SAFETIES: THE CONTRACTOR SHALL SHOW EACH PROOF AND SAFETY AS A SEPARATE ROW.
3) | SYS-OCC: AS DESCRIBED IN THE POINTS SCHEDULE INSTRUCTIONS, OVERRIDE OF SYS-OCC IS ACCOMPLISHED THROUGH THE SYSTEM SCHEDULER.
4) | ALARM CONDITIONS MARKED WITH AN ASTERISK (*) SHALL BE ACTIVE ONLY WHEN THE SYSTEM IS IN OCCUPIED MODE AND HAS BEEN IN OCCUPIED MODE FOR MORE THAN: * = 5 MINUTES ** = 30 MINUTES
5) | UNIT STATUS: SERVES AS A MONITORED POINT AT THE M&C SOFTWARE (FRONT-END) AND AS A HEATING/COOLING REQUEST TO THE BOILER, HEAT EXCHANGER, AND/OR CHILLER SERVING THIS SYSTEM.